## Hoja2 (hidden)
Listas
1 | 1 | 3 |  |  |  |  | 1
patm/altura | correción | caudales |  |  |  |  | caudales
bar | FAD a Normal | l/s (FAD) | 1 | l/s (FAD) | Nl/s | Sl/s | Nl/s | 1 | Nl/s | Sl/s | l/s (FAD) | Sl/s | l/s (FAD) | Nl/s
m.s.n.m. | FAD a Standard | l/min (FAD) | 2 | l/min (FAD) | Nl/min | Sl/min | Nl/min | 2 | Nl/min | Sl/min | l/min (FAD) | Sl/min | l/min (FAD) | Nl/min
| Normal a FAD | m³/h (FAD) | 3 | m³/h (FAD) | Nm³/h | Sm³/h | Nm³/h | 3 | Nm³/h | Sm³/h | m³/h (FAD) | Sm³/h | m³/h (FAD) | Nm³/h
| Normal a Standard | m³/min (FAD) | 4 | m³/min (FAD) | Nm³/min | Sm³/min | Nm³/min | 4 | Nm³/min | Sm³/min | m³/min (FAD) | Sm³/min | m³/min (FAD) | Nm³/min
| Standard a FAD | cfm (FAD) | 5 | cfm (FAD) | Ncfm | Scfm | Ncfm | 5 | Ncfm | Scfm | cfm (FAD) | Scfm | cfm (FAD) | Ncfm
| Standard a Normal | gpm (FAD) | 6 | gpm (FAD) | Ngpm | Sgpm | Ngpm | 6 | Ngpm | Sgpm | gpm (FAD) | Sgpm | gpm (FAD) | Ngpm

## Info2 (hidden)
CLICK AQUÍ PARA VOLVER A MENÚ PRINCIPAL
Atlas Copco utiliza las siguientes condiciones de referencia para la condición Standard:
Condición Standard ASME
Presión atmosférica | 1.013 | bar(atm)
Humedad Relativa | 36 | %
Temperatura | 20 | °C
Condición Standard CAGI
Presión atmosférica | 1 | bar(atm)
Humedad Relativa | 0 | %
Temperatura | 20 | °C
Condición Standard Canada
Presión atmosférica | 1.013 | bar(atm)
Humedad Relativa | 0 | %
Temperatura | 21.11 | °C
Condición Standard US
Presión atmosférica | 1.013 | bar(atm)
Humedad Relativa | 0 | %
Temperatura | 15.56 | °C
Estas condiciones pueden variar dependiendo de lo establecido por el usuario. Para utilizar
otras condiciones de referencia, sólo se debe cambiar los valores en el menú principal.

## Info (hidden)
CLICK AQUÍ PARA VOLVER A MENÚ PRINCIPAL
Atlas Copco utiliza las siguientes condiciones de referencia para la condición Normal:
Condición Normal
Presión atmosférica | 1.013 | bar(atm)
Humedad Relativa | 0 | %
Temperatura | 0 | °C
Estas condiciones pueden variar dependiendo de lo establecido por el usuario. Para utilizar
otras condiciones de referencia, sólo se debe cambiar los valores en el menú principal.

## FAD to Norm code
Function for a FAD to Normal transformation
Function to transform a volume flow rate from FAD conditions
to a Normal state conditions
VN = | FADtoNORMAL( Patm_bar,tamb,RHamb%,Vreq) |  |  |  | FAD (Free Air Delivery) (f.a.d) is the actual
quantity of compressed air converted back
VN : Value of the given air flow rate "Vreq" , |  |  |  | m3/h (FAD) | to the inlet conditions of the compressor.
expressed in Normal conditions. For example, in Nl/s
Site conditions: Inlet conditions of the compressor.
Compressor inlet conditions: |  |  | (FAD conditions) |  | Patm_bar : Ambient air absolute pressure [bar]
Patm_bar = | 2 | bar |  |  | tamb: Ambiente air temperature [ºC]
tamb = | 5 | ºC |  |  | RHamb% : Ambient air relative humidity [%]
RHamb% = | 24 | % |  |  | VFAD : Compressed air volume flow rate
expresed with the site conditions [m3/h (FAD)]
Free Air Delivery flow rate
Air flowrate at compressor inlet (at site conditions) |  |  |  |  | VN : Value of the given air flow rate "Vreq"
Vreq = | 480 | m3/h (FAD) |  |  | expressed in Normal conditions [Nl/s]
Normal Conditions
Equivalent flow rate expresed in Normal Conditions
using the function: FADtoNORMAL
VN = | 258.2417 | Nl/s | (Normal liters per second)

## Step by step calculation
1 of 3
1.- Data |  |  | 2.- Atmospheric data. |  |  |  | 3.- Normal State 2 |  |  |  | State 1: FAD state |  |  |  | FAD vapor pressure
(a) Site conditions |  |  | State 1: FAD | [7 empty] | T1 = | 278.15 | K |  | Pv1 = | RH1 * Psat1
Patm = | 2 | bar |  |  |  |  | Normal pressure |  |  |  | P1 = | 200000 | Pa |  | RH1 = | 0.24 | -
tamb = | 5 | ºC | Atmospheric pressure |  |  |  | P2 = | 101300 | Pa |  | RH1 = | 0.24 | - |  | Psat1 = | 872.5541 | bar
RH% = | 24 | % | P1 = | 200000 | Pa | [5 empty] | Psat1 = | 872.5541 | Pa |  | Pv1 = | 209.413 | Pa
Relative humidity normal air
(b) Required volume flow rate |  |  | Relative humidity atmospheric air |  |  |  | RH2 = | RH2%/100 |  |  | Water sat pressure at Normal cond.
Vrequerido = | 480 | m3/h (FAD) | RH1 = | RH1%/100 |  |  | RH2% = | 0 | % |  | Psat=SaturatedWaterPressure_t(t) |  |  |  | Dry air partial pressure
|  |  | RH1% = | 24 | % |  | RH2 = | 0 | - |  | t2 = | 0 | ºC |  | Pda = | Patm - Pv
(c) Normal conditions |  |  | RH1 = | 0.24 | - | [5 empty] | Psat2 = | 611.2912 | Pa |  | Patm = | 200000 | Pa
tN = | 0 | ºC |  |  |  |  | Air normal temperature | [7 empty] | Pv = | 209.413 | Pa
PN = | 1.013 | bar | Temperature atmospheric air |  |  |  | t2 = | 0 | ºC |  | State 2: Normal state |  |  |  | Pda = | 199790.587 | Pa
RHN = | 0 | % | t1 = | 5 | ºC |  | T2 = | 273.15 | K |  | T2 = | 273.15 | K
|  |  | T1 = | 278.15 | K | [5 empty] | P2 = | 101300 | Pa |  | Vapor pressure in normal
(d) Constants | [6 empty] | Water sat pressure at |  |  |  | RH2 = | 0 | - |  | state
Dry air constant | [6 empty] | ambient temp |  |  |  | Psat2 = | 611.2912 | Pa |  | Pv2 = | RH2 * Psat2
Rda = | 287.05 | [J/(kg*K)] | Result of step by |  |  |  | Psat =SaturatedWaterPressure_t(t) | [7 empty] | RH2 = | 0 | -
Water constant |  |  | step calculation |  |  |  | t1 = | 5 | ºC | [5 empty] | Psat2 = | 611.2912 | bar
Rw = | 461.495 | [J/(kg*K)] | VN = | 258.2417 | Nl/s |  | Psat1 = | 872.5541 | Pa | [5 empty] | Pv2 = | 0 | Pa
Kelvin
Kelv = | 273.15 | K
2 of 3
Density of wet air at site conditions |  |  |  | Mass flow rate | [5 empty] | FAD(1) to Normal(2)
rwa = | (Pv/Rw+ Pda/Rda ) / TSite |  |  | mwa = | Vreq * rwa
Pv1 = | 209.413 | Pa |  | Vreq = | 480 | m3/h (FAD)
Rw = | 461.495 | [J/(kg*K)] |  | rwa = | 2.5039 | kg/m3
Pda = | 199790.587 | Pa |  | mwa = | 1201.8844 | kg/h |  |  |  | Stte 1 is FAD
Rda = | 287.05 | [J/(kg*K)] |  | mwa = | 0.33386 | kg/s |  |  |  | FAD volume flow rate
T = | 278.15 | K | [7 empty] | V1 = | 133.3333 | l/s (FAD)
rwa = | 2.5039 | kg/m3 |  | Transformation of the required | [5 empty] | State 2 is Normal State
|  |  |  | flow rate Vreq [ m3/h (FAD) ] | [5 empty] | V2 = V1*(T2/T1)*( P1-RH1*Psat1) / ( P2-RH2*Psat2 )
Density of normal air |  |  |  | into l/s (FAD) | [5 empty] | T2 = | 273.15 | K
p *v = | Rda * TN | [8 empty] | T1 = | 278.15 | K
rda_N = | PN / (Rda * TN) |  |  | 1 m3/h = | 1000/3600 | l/s |  |  |  | P1 = | 200000 | Pa
PN = | 101300 | Pa |  | 1 m3/h = | 0.27778 | l/s |  |  |  | P2 = | 101300 | Pa
Rda = | 287.05 | [J/(kg*K)] |  | UT = | 0.27778 |  |  |  |  | RH1 = | 0.24 | -
TN = | 273.15 | K |  | Vreq = | 480 | m3/h (FAD) |  |  |  | RH2 = | 0 | -
rda_N = | 1.292 | kg/m3 |  | V1 = | Vrequerido | (m3h / l/s) |  |  |  | Psat1 = | 872.5541 | Pa
|  |  |  | V1 = | 480 | 0.27778 |  |  |  | Psat2 = | 0 | Pa
|  |  |  | V1 = | 133.3333 | l/s (Fad) |  |  |  | V2 = | 258.2417 | Nl/s
3 of 3
Example solved with Atlas Copco program | [12 empty] | Example solved with a
step by step calculation
(a) Site conditions
[13 empty] | Patm = | 2 | bar (a)
[13 empty] | RH% = | 24 | %
[13 empty] | tamb = | 5 | ºC
(b) Required volume flow rate
[13 empty] | Vrequerido = | 480 | m3/h (FAD)
Resultant flow in normal conditions
[13 empty] | V2 = | 258.2417 | Nl/s
*
*

## Atlas Copco
[1]
Seleccionar Cálculo
Condiciones de Sitio |  |  | Condición Normal | más info click aquí
Presión atmosférica/altura | 2 |  | Presión atmosférica | 1.013 | bar(atm)
Humedad Relativa | 24 | % | Humedad Relativa | 0 | %
Temperatura | 5 | °C | Temperatura | 0 | °C
Operación |  |  | Condición Standard | más info click aquí
Caudal requerido | 480 |  | Presión atmosférica | 1.013 | bar(atm)
|  |  | Humedad Relativa | 0 | %
|  |  | Temperatura | 15.56 | °C
Resultado
Caudal corregido | 258.24 |  | ROUNDUP(Hoja3!B48,2)
Masa | 0.33404 | kg/s
Presión atm. del sitio | 2 | bar(a)
Ecuación utilizada
P[i]: Presión atmosférica [i]
RH[i]: Humedad relativa [i]
Psat@T[i]: Presión de saturación a temperatura [i]
V[i]: Volumen [i]
T[i]: Temperatura [i]
Sub Listadesplegable2_AlCambiar()
Dim a, b As Double
ActiveWorkbook.Sheets(2).Activate
b = Range("a2")
ActiveWorkbook.Sheets(1).Activate
a = Range("D7")
If b = 1 And a < 0.19 Then
MsgBox "Ingresa un valor entre 0,2 y 1,013 bar(a)."
a = 1.013
Range("D7") = a
End If
If b = 1 And a > 1.014 Then
MsgBox "Ingresa un valor entre 0,2 y 1,013 bar(a)."
a = 1.013
Range("D7") = a
End If
If b = 2 And a > 6000 Then
MsgBox "Ingresa un valor entre 0 y 6.000 m.s.n.m."
a = 0
Range("D7") = a
End If
If b = 2 And a < 0 Then
MsgBox "Ingresa un valor entre 0 y 6.000 m.s.n.m."
a = 0
Range("D7") = a
End If
End S

## Hoja3
Sitio | [7 empty] | Temp | pS
Patm | 2 | [6 empty] | °C | mbar
T(°K) | 278 | [6 empty] | -100 | 1.403e-05
Psat (bar) | 0.00872 | [6 empty] | -99 | 1.719e-05
RH | 0.24 | [6 empty] | -98 | 2.101e-05
[8 empty] | -97 | 2.561e-05
R(dry) | 287.05 | [6 empty] | -96 | 3.117e-05
R(wet) | 461.495 | [6 empty] | -95 | 3.784e-05
|  | Normal | STD |  |  |  |  | -94 | 4.584e-05
Pd | 0.0020928 | 0 | 0 |  |  |  |  | -93 | 5.542e-05
[8 empty] | -92 | 6.685e-05
[8 empty] | -91 | 8.049e-05
[8 empty] | -90 | 9.672e-05
|  | Normal | STD |  |  |  |  | -89 | 0.000116
Pg | 1.9979 | 1.013 | 1.013 |  |  |  |  | -88 | 0.0001388
[8 empty] | -87 | 0.0001658
|  | Normal | STD |  |  |  |  | -86 | 0.0001977
Rho | 2.5053 | 1.2927 | 1.223 |  |  |  |  | -85 | 0.0002353
[8 empty] | -84 | 0.0002796
[8 empty] | -83 | 0.0003316
[6 empty] | Do not delete this sheet |  | -82 | 0.0003925
[6 empty] | It is used by the Atlas Copco calculation |  | -81 | 0.0004638
[8 empty] | -80 | 0.0005473
[8 empty] | -79 | 0.0006444
[8 empty] | -78 | 0.0007577
|  | l/s | l/min | m³/h | m³/min | cfm | gpm | -77 | 0.0008894
1 | l/s | 1 | 60 | 3.6 | 0.06 | 2.1189 | 15.8503 | -76 | 0.001042
2 | l/min | 0.016667 | 1 | 0.06 | 0.001 | 0.035315 | 0.26417 | -75 | 0.00122
3 | m³/h | 0.27778 | 16.6667 | 1 | 0.016667 | 0.58858 | 4.4029 | -74 | 0.001426
4 | m³/min | 16.6667 | 1000 | 60 | 1 | 35.3147 | 264.1721 | -73 | 0.001665
5 | cfm | 0.47195 | 28.3168 | 1.699 | 0.028317 | 1 | 7.4805 | -72 | 0.001936
6 | gpm | 0.06309 | 3.7854 | 0.22712 | 0.0037854 | 0.13368 | 1 | -71 | 0.002252
[8 empty] | -70 | 0.002615
Transf. | 133.3333 | l/s | [5 empty] | -69 | 0.003032
| Normal | Std (US) | FAD sitio |  |  |  |  | -68 | 0.003511
Psat | 0.00611 | 0.01704 | 0.00872 |  |  |  |  | -67 | 0.00406
P atm | 1.013 | 1.013 | 2 |  |  |  |  | -66 | 0.00688
H Relativa | 0 | 0 | 0.24 |  |  |  |  | -65 | 0.005406
Temperatura | 273 | 288.56 | 278 |  |  |  |  | -64 | 0.006225
QN(l/s) | 133.3333 | 126.1436 | 258.2394 |  |  |  |  | -63 | 0.007159
Q(l/s) | 68.8422 | 65.1301 | 133.3333 |  |  |  |  | -62 | 0.008223
QS(l/s) | 140.9328 | 133.3333 | 272.9581 |  |  |  |  | -61 | 0.0094332
[8 empty] | -60 | 0.0108
m(kg/s) | 0.17247 | 0.16317 | 0.33404 |  |  |  |  | -59 | 0.01236
[8 empty] | -58 | 0.01413
Transf. | 258.2394 | 272.9581 | 68.8422 | 140.9328 | 65.1301 | 126.1436 |  | -57 | 0.1612
Transf. Masa | 0.33404 | 0.33404 | 0.17247 | 0.17247 | 0.16317 | 0.16317 |  | -56 | 0.01838
Seleccionado | 258.2394 | [6 empty] | -55 | 0.02092
Selecc. Masa | 0.33404 | [6 empty] | -54 | 0.0238
[8 empty] | -53 | 0.02703
[8 empty] | -52 | 0.03067
[8 empty] | -51 | 0.03476
[8 empty] | -50 | 0.03935
[8 empty] | -49 | 0.04449
[5 empty] | Do not delete this sheet |  |  | -48 | 0.05026
[5 empty] | It is used by the Atlas Copco calculation |  |  | -47 | 0.05671
[8 empty] | -46 | 0.06393
[8 empty] | -45 | 0.07198
[8 empty] | -44 | 0.08097
[8 empty] | -43 | 0.09098
[8 empty] | -42 | 0.1021
[8 empty] | -41 | 0.1145
[8 empty] | -40 | 0.1283
[8 empty] | -39 | 0.1436
[8 empty] | -38 | 0.1606
[8 empty] | -37 | 0.1794
[8 empty] | -36 | 0.2002
[8 empty] | -35 | 0.2233
[8 empty] | -34 | 0.2488
[8 empty] | -33 | 0.2769
[8 empty] | -32 | 0.3079
[8 empty] | -31 | 0.3421
[8 empty] | -30 | 0.38
[8 empty] | -29 | 0.421
[8 empty] | -28 | 0.467
[8 empty] | -27 | 0.517
[8 empty] | -26 | 0.572
[8 empty] | -25 | 0.632
[8 empty] | -24 | 0.689
[8 empty] | -23 | 0.771
[8 empty] | -22 | 0.85
[8 empty] | -21 | 0.937
[8 empty] | -20 | 1.03
[8 empty] | -19 | 1.14
[8 empty] | -18 | 1.25
[8 empty] | -17 | 1.37
[8 empty] | -16 | 1.51
[8 empty] | -15 | 1.65
[8 empty] | -14 | 1.81
[8 empty] | -13 | 1.98
[8 empty] | -12 | 2.17
[8 empty] | -11 | 2.38
[8 empty] | -10 | 2.6
[8 empty] | -9 | 2.84
[8 empty] | -8 | 3.1
[8 empty] | -7 | 3.38
[8 empty] | -6 | 3.69
[8 empty] | -5 | 4.02
[8 empty] | -4 | 4.37
[8 empty] | -3 | 4.76
[8 empty] | -2 | 5.17
[8 empty] | -1 | 5.62
[8 empty] | 0 | 6.11
[8 empty] | 1 | 6.57
[8 empty] | 2 | 7.06
[8 empty] | 3 | 7.58
[8 empty] | 4 | 8.13
[8 empty] | 5 | 8.72
[8 empty] | 6 | 9.35
[8 empty] | 7 | 10.01
[8 empty] | 8 | 10.72
[8 empty] | 9 | 11.47
[8 empty] | 10 | 12.27
[8 empty] | 11 | 13.12
[8 empty] | 12 | 14.02
[8 empty] | 13 | 14.97
[8 empty] | 14 | 15.98
[8 empty] | 15 | 17.04
[8 empty] | 16 | 18.17
[8 empty] | 17 | 19.37
[8 empty] | 18 | 20.63
[8 empty] | 19 | 21.96
[8 empty] | 20 | 23.37
[8 empty] | 21 | 24.86
[8 empty] | 22 | 26.43
[8 empty] | 23 | 28.09
[8 empty] | 24 | 29.83
[8 empty] | 25 | 31.67
[8 empty] | 26 | 33.61
[8 empty] | 27 | 35.65
[8 empty] | 28 | 37.8
[8 empty] | 29 | 40.06
[8 empty] | 30 | 42.43
[8 empty] | 31 | 44.93
[8 empty] | 32 | 47.55
[8 empty] | 33 | 50.31
[8 empty] | 34 | 53.2
[8 empty] | 35 | 56.24
[8 empty] | 36 | 59.42
[8 empty] | 37 | 62.76
[8 empty] | 38 | 66.28
[8 empty] | 39 | 69.93
[8 empty] | 40 | 73.78
[8 empty] | 41 | 77.8
[8 empty] | 42 | 82.02
[8 empty] | 43 | 86.42
[8 empty] | 44 | 91.03
[8 empty] | 45 | 95.86
[8 empty] | 46 | 100.9
[8 empty] | 47 | 106.2
[8 empty] | 48 | 111.7
[8 empty] | 49 | 117.4
[8 empty] | 50 | 123.4
[8 empty] | 51 | 129.7
[8 empty] | 52 | 136.2
[8 empty] | 53 | 143
[8 empty] | 54 | 150.1
[8 empty] | 55 | 157.5
[8 empty] | 56 | 165.2
[8 empty] | 57 | 173.2
[8 empty] | 58 | 181.5
[8 empty] | 59 | 190.2
[8 empty] | 60 | 199.2
[8 empty] | 61 | 208.6
[8 empty] | 62 | 218.4
[8 empty] | 63 | 228.5
[8 empty] | 64 | 239.1
[8 empty] | 65 | 250.1
[8 empty] | 66 | 261.5
[8 empty] | 67 | 273.3
[8 empty] | 68 | 285.6
[8 empty] | 69 | 298.4
[8 empty] | 70 | 311.6
[8 empty] | 71 | 325.3
[8 empty] | 72 | 339.6
[8 empty] | 73 | 354.3
[8 empty] | 74 | 369.6
[8 empty] | 75 | 385.5
[8 empty] | 76 | 401.9
[8 empty] | 77 | 418.9
[8 empty] | 78 | 436.5
[8 empty] | 79 | 454.7
[8 empty] | 80 | 473.6
[8 empty] | 81 | 493.1
[8 empty] | 82 | 513.3
[8 empty] | 83 | 534.2
[8 empty] | 84 | 555.7
[8 empty] | 85 | 578
[8 empty] | 86 | 601
[8 empty] | 87 | 624.9
[8 empty] | 88 | 649.5
[8 empty] | 89 | 674.9
[8 empty] | 90 | 701.1
[8 empty] | 91 | 728.2
[8 empty] | 92 | 756.1
[8 empty] | 93 | 784.9
[8 empty] | 94 | 814.6
[8 empty] | 95 | 845.3
[8 empty] | 96 | 876.9
[8 empty] | 97 | 909.4
[8 empty] | 98 | 943
[8 empty] | 99 | 977.6
[8 empty] | 100 | 1013.2
[8 empty] | 101 | 1050
[8 empty] | 102 | 1088
[8 empty] | 103 | 1127
[8 empty] | 104 | 1167
[8 empty] | 105 | 1208
[8 empty] | 106 | 1250
[8 empty] | 107 | 1294
[8 empty] | 108 | 1339
[8 empty] | 109 | 1385
[8 empty] | 110 | 1433
[8 empty] | 111 | 1481
[8 empty] | 112 | 1532
[8 empty] | 113 | 1583
[8 empty] | 114 | 1636
[8 empty] | 115 | 1691
[8 empty] | 116 | 1746
[8 empty] | 117 | 1804
[8 empty] | 118 | 1863
[8 empty] | 119 | 1923
[8 empty] | 120 | 1985
[8 empty] | 121 | 2049
[8 empty] | 122 | 2114
[8 empty] | 123 | 2182
[8 empty] | 124 | 2250
[8 empty] | 125 | 2321
[8 empty] | 126 | 2393
[8 empty] | 127 | 2467
[8 empty] | 128 | 2543
[8 empty] | 129 | 2621
[8 empty] | 130 | 2701
[8 empty] | 131 | 2783
[8 empty] | 132 | 2867
[8 empty] | 133 | 2953
[8 empty] | 134 | 3041
[8 empty] | 135 | 3131
[8 empty] | 136 | 3223
[8 empty] | 137 | 3317
[8 empty] | 138 | 3414
[8 empty] | 139 | 3512
[8 empty] | 140 | 3614
[8 empty] | 141 | 3722.2
[8 empty] | 142 | 3830.4
[8 empty] | 143 | 3938.6
[8 empty] | 144 | 4046.8
[8 empty] | 145 | 4155
[8 empty] | 146 | 4276
[8 empty] | 147 | 4397
[8 empty] | 148 | 4518
[8 empty] | 149 | 4639
[8 empty] | 150 | 4760
[8 empty] | 151 | 4894.6
[8 empty] | 152 | 5029.2
[8 empty] | 153 | 5163.8
[8 empty] | 154 | 5298.4
[8 empty] | 155 | 5433
[8 empty] | 156 | 5582.6
[8 empty] | 157 | 5732.2
[8 empty] | 158 | 5881.8
[8 empty] | 159 | 6031.4
[8 empty] | 160 | 6181
[8 empty] | 161 | 6346.4
[8 empty] | 162 | 6511.8
[8 empty] | 163 | 6677.2
[8 empty] | 164 | 6842.6
[8 empty] | 165 | 7008
[8 empty] | 166 | 7190.4
[8 empty] | 167 | 7372.8
[8 empty] | 168 | 7555.2
[8 empty] | 169 | 7737.6
[8 empty] | 170 | 7920
[8 empty] | 171 | 8120.8
[8 empty] | 172 | 8321.6
[8 empty] | 173 | 8522.4
[8 empty] | 174 | 8723.2
[8 empty] | 175 | 8924
[8 empty] | 176 | 9144.6
[8 empty] | 177 | 9365.2
[8 empty] | 178 | 9585.8
[8 empty] | 179 | 9806.4
[8 empty] | 180 | 10027
[8 empty] | 181 | 10268.2
[8 empty] | 182 | 10509.4
[8 empty] | 183 | 10750.6
[8 empty] | 184 | 10991.8
[8 empty] | 185 | 11233
[8 empty] | 186 | 11496.6
[8 empty] | 187 | 11760.2
[8 empty] | 188 | 12023.8
[8 empty] | 189 | 12287.4
[8 empty] | 190 | 12551
[8 empty] | 191 | 12838.2
[8 empty] | 192 | 13125.4
[8 empty] | 193 | 13412.6
[8 empty] | 194 | 13699.8
[8 empty] | 195 | 13987
[8 empty] | 196 | 14299.4
[8 empty] | 197 | 14611.8
[8 empty] | 198 | 14924.2
[8 empty] | 199 | 15236.6
[8 empty] | 200 | 15549
[8 empty] | 201 | 15887.8
[8 empty] | 202 | 16226.6
[8 empty] | 203 | 16565.4
[8 empty] | 204 | 16904.2
[8 empty] | 205 | 17243
[8 empty] | 206 | 17609.8
[8 empty] | 207 | 17976.6
[8 empty] | 208 | 18343.4
[8 empty] | 209 | 18710.2
[8 empty] | 210 | 19077
[8 empty] | 211 | 19473.6
[8 empty] | 212 | 19870.2
[8 empty] | 213 | 20266.8
[8 empty] | 214 | 20663.4
[8 empty] | 215 | 21060
[8 empty] | 216 | 21487.6
[8 empty] | 217 | 21915.2
[8 empty] | 218 | 22342.8
[8 empty] | 219 | 22770.4
[8 empty] | 220 | 23198
[8 empty] | 221 | 23658.6
[8 empty] | 222 | 24119.2
[8 empty] | 223 | 24579.8
[8 empty] | 224 | 25040.4
[8 empty] | 225 | 25501
[8 empty] | 226 | 25996
[8 empty] | 227 | 26491
[8 empty] | 228 | 26986
[8 empty] | 229 | 27481
[8 empty] | 230 | 27976
[8 empty] | 231 | 28507.2
[8 empty] | 232 | 29038.4
[8 empty] | 233 | 29569.6
[8 empty] | 234 | 30100.8
[8 empty] | 235 | 30632
[8 empty] | 236 | 31201.2
[8 empty] | 237 | 31770.4
[8 empty] | 238 | 32339.6
[8 empty] | 239 | 32908.8
[8 empty] | 240 | 33478
[8 empty] | 241 | 34087
[8 empty] | 242 | 34696
[8 empty] | 243 | 35305
[8 empty] | 244 | 35914
[8 empty] | 245 | 36523
[8 empty] | 246 | 37173.6
[8 empty] | 247 | 37824.2
[8 empty] | 248 | 38474.8
[8 empty] | 249 | 39125.4
[8 empty] | 250 | 39776
[8 empty] | 251 | 40470
[8 empty] | 252 | 41164
[8 empty] | 253 | 41858
[8 empty] | 254 | 42552
[8 empty] | 255 | 43246
[8 empty] | 256 | 43985.4
[8 empty] | 257 | 44724.8
[8 empty] | 258 | 45464.2
[8 empty] | 259 | 46203.6
[8 empty] | 260 | 46943
[8 empty] | 261 | 47729.8
[8 empty] | 262 | 48516.6
[8 empty] | 263 | 49303.4
[8 empty] | 264 | 50090.2
[8 empty] | 265 | 50877
[8 empty] | 266 | 51713.2
[8 empty] | 267 | 52549.4
[8 empty] | 268 | 53385.6
[8 empty] | 269 | 54221.8
[8 empty] | 270 | 55058
[8 empty] | 271 | 55945.6
[8 empty] | 272 | 56833.2
[8 empty] | 273 | 57720.8
[8 empty] | 274 | 58608.4
[8 empty] | 275 | 59496
[8 empty] | 276 | 60437.2
[8 empty] | 277 | 61378.4
[8 empty] | 278 | 62319.6
[8 empty] | 279 | 63260.8
[8 empty] | 280 | 64202
[8 empty] | 281 | 65198.8
[8 empty] | 282 | 66195.6
[8 empty] | 283 | 67192.4
[8 empty] | 284 | 68189.2
[8 empty] | 285 | 69186
[8 empty] | 286 | 70241
[8 empty] | 287 | 71296
[8 empty] | 288 | 72351
[8 empty] | 289 | 73406
[8 empty] | 290 | 74461
[8 empty] | 291 | 75576.2
[8 empty] | 292 | 76691.4
[8 empty] | 293 | 77806.6
[8 empty] | 294 | 78921.8
[8 empty] | 295 | 80037
[8 empty] | 296 | 81215
[8 empty] | 297 | 82393
[8 empty] | 298 | 83571
[8 empty] | 299 | 84749
[8 empty] | 300 | 85927

## VBA code
VBA code
Function FADtoNORMAL(Patm_bar, tamb, RHamb%, Vreq)
' 17.12.2021
'This function transform a FAD volume flow rate
'ito its corresponding Normal State value.
' Normal conditions
TNc = | 0 | ºC
PN_bar = | 1.013 | bar | (absolute pressure)
RHN% = | 0 | %
' Constants
'Dry air constant
Rda = 287.05 '[J/(kg*K)]
'Water constant
Rw = 461.495 '[J/(kg*K)]
'Kelvin
Kelv = 273.15
' Atmospheric data. State 1: FAD
' atmospheric pressure
Patm = Patm_bar * 100 * 1000 'Pa
P1 = Patm 'Pa
' Relative humidity atmospheric air
RH1 = RHamb% / 100 ' -
'Temperature atmospheric air
T1c = tamb 'ºC
T1 = T1c + Kelv ' K
' Normal State 2
' Normal pressure an temperature
PN = PN_bar * 100 * 1000 'Pa
P2 = PN 'Pa
TN = TNc + Kelv 'K
'Relative humidity normal air
RH2 = RHN% / 100 ' -
' Air normal temperature
T2c = TNc ' ºC
T2 = T2c + Kelv ' K
Water sat pressure at Normal conditions
Psat2 = SaturatedWaterIcePressure_t(T2c) 'Pa
' Site consitions State 1
'( Water sat pressure at ambient(1) temp
Psat1 = SaturatedWaterIcePressure_t(T1c) 'Pa
' FAD vapor pressure
Pv1 = RH1 * Psat1 'Pa
' Dry air partial pressure
Pda = Patm - Pv1 'Pa
' Normal vapor pressure
Pv2 = RH2 * Psat2 'Pa
' Density of wet air at site conditions
RHOwa = (Pv1 / Rw + Pda / Rda) / T1 'kg/m3
'Density of normal air
RHOda_N = PN / (Rda * TN)
'Mass flow rate
mwa = Vreq * RHOwa
' V1 (l/s(fad)
UT = 0.277777778 '(l/s) / (M3/h)
V1 = Vreq * UT 'l/s (FAD)
'State 2 is Normal State
V2 = V1 * (T2 / T1) * (P1 - RH1 * Psat1) / (P2 - RH2 * Psat2)
FADtoNORMAL = V2
End Function

## Ref
[1] | This file was sent via email by an Atlas Copco engineer, without any additional reference. It is simply a file for internal use by this company.

## Atlas Copco subroutine (hidden)
Sub Listadesplegable2_AlCambiar() | This subroutine ckeck if the entered value of the atmospheric ptessure, in the defined pressure unit, is in the valid range
Dim a, b As Double
|  | If pressure is bar | b = 1 | sheet(2), Range("a2") = b = | 1 | bar
ActiveWorkbook.Sheets(2).Activate | In sheet(2), Range("a2") | If pressure is m.a.s.l. | b = 2 | sheet(2), Range("a2") = b = | 2 | m.a.s.l.
b = Range("a2")
ActiveWorkbook.Sheets(1).Activate | In sheet(1), Range("d7") | Atmospheric prresure value
a = Range("D7") |  | expressed in the selected unit
If b = 1 And a < 0.19 Then | If the pressure is in bar (b=1), the valid accepted atmospheric pressure range is 0.19 bar < patm < 1.013 bar
MsgBox "Ingresa un valor entre 0,2 y 1,013 bar(a)." | If the entered value is less than 0.19 bar, a mesage indicates the the pressure range is: 0.2 bar < Patm < 1.013 bar
a = 1.013 | In this case, the atmospheric pressure is set to a = Patm = 1.013, and Cell ("D7) will show the value of "a"
Range("D7") = a
End If
If b = 1 And a > 1.014 Then | If the pressure is in bar (b=1), the valid accepted atmospheric pressure range is 0.19 bar < patm < 1.013 bar
MsgBox "Ingresa un valor entre 0,2 y 1,013 bar(a)." | If the entered value is grather than 1.013 bar, a mesage indicates the the pressure range is: 0.2 bar < Patm < 1.013 bar
a = 1.013 | In this case, the atmospheric pressure is set to a = Patm = 1.013, and Cell ("D7) will show the value of "a"
Range("D7") = a
End If
If b = 2 And a > 6000 Then | If the pressure is in m.a.s.l (b=2), the valid accepted atmospheric pressure range is 0.0 m.a.s.l. < patm < 6000 m.a.s.l
MsgBox "Ingresa un valor entre 0 y 6.000 m.s.n.m." | If the entered value is grather than 6000 m.a.s.l., a mesage indicates the the pressure range is: 0.0 m.a.s.l. < Patm < 6000 m.a.s.l.
a = 0 | In this case, the atmospheric pressure is set to a = Patm = 0.0 m.a.s.l, and Cell ("D7) will show the value of "a"
Range("D7") = a
End If
If b = 2 And a < 0 Then | If the pressure is in m.a.s.l (b=2), the valid accepted atmospheric pressure range is 0.0 m.a.s.l. < patm < 6000 m.a.s.l
MsgBox "Ingresa un valor entre 0 y 6.000 m.s.n.m." | If the entered value is less than 0.0 m.a.s.l., a mesage indicates the the pressure range is: 0.0 m.a.s.l. < Patm < 6000 m.a.s.l.
a = 0 | In this case, the atmospheric pressure is set to a = Patm = 0.0 m.a.s.l, and Cell ("D7) will show the value of "a"
Range("D7") = a
End If
Subroutine_to_ckeck_entered_values
End Sub

## Water Data (hidden)
0 | 0.569 | 4.217 | 12.99 | 1000 | 0.00175 | 1.75e-06 | 1.3493e-07 | 0.006108
1.85 | 0.574 | 4.211 | 12.22 | 1000 | 0.001652 | 1.652e-06 | 1.3631e-07 | 0.0069793 |  | Application example
6.85 | 0.582 | 4.198 | 10.26 | 1000 | 0.001422 | 1.422e-06 | 1.3864e-07 | 0.0099092
11.85 | 0.59 | 4.189 | 8.81 | 1000 | 0.001225 | 1.225e-06 | 1.4085e-07 | 0.013876 |  | Input data: Temperature | t = | 35 | ºC
16.85 | 0.598 | 4.184 | 7.56 | 999.001 | 0.00108 | 1.0811e-06 | 1.4307e-07 | 0.019178
21.85 | 0.606 | 4.181 | 6.62 | 998.004 | 0.000959 | 9.6092e-07 | 1.4523e-07 | 0.026181 |  | Function used |  | Results
26.85 | 0.613 | 4.179 | 5.83 | 997.009 | 0.000855 | 8.5756e-07 | 1.4713e-07 | 0.035323 |  | SaturatedWaterConductivity_t | k = | 0.625 | W/(m*K)
31.85 | 0.62 | 4.178 | 5.2 | 995.0249 | 0.000769 | 7.7284e-07 | 1.4914e-07 | 0.047132 |  | SaturatedWaterSpecificHeat_t | Cp = | 4.178 | kJ/kg
36.85 | 0.628 | 4.178 | 4.62 | 993.0487 | 0.000695 | 6.9986e-07 | 1.5136e-07 | 0.062228 |  | SaturatedWaterPrandtl_t | Pr = | 4.835 | -
41.85 | 0.634 | 4.179 | 4.16 | 991.0803 | 0.000631 | 6.3668e-07 | 1.5308e-07 | 0.081341 |  | SaturatedWaterDensity_t | r = | 993.7798 | kg/m3
46.85 | 0.64 | 4.18 | 3.77 | 989.1197 | 0.000577 | 5.7758e-07 | 1.5326e-07 | 0.10532 |  | SaturatedWaterAbsoluteViscosity_t | m = | 0.00072238 | Pa*s
51.85 | 0.645 | 4.182 | 3.42 | 987.1668 | 0.000528 | 5.3486e-07 | 1.5624e-07 | 0.13513 |  | SaturatedWaterKinematicViscosity_t | n = | 7.269e-07 | m2/s
56.85 | 0.651 | 4.184 | 3.15 | 984.252 | 0.000489 | 4.9682e-07 | 1.5784e-07 | 0.1719 |  | SaturatedWaterThermalDiffusivity_t | a = | 1.505e-07 | m2/s
61.85 | 0.656 | 4.186 | 2.88 | 982.3183 | 0.000453 | 4.6115e-07 | 1.5953e-07 | 0.21689
66.85 | 0.66 | 4.188 | 2.66 | 979.4319 | 0.00042 | 4.2882e-07 | 1.609e-07 | 0.27153
71.85 | 0.664 | 4.191 | 2.45 | 976.5625 | 0.000389 | 3.9834e-07 | 1.6321e-07 | 0.33742
76.85 | 0.668 | 4.195 | 2.29 | 973.7098 | 0.000365 | 3.7485e-07 | 1.6354e-07 | 0.41632
81.85 | 0.671 | 4.199 | 2.14 | 970.8738 | 0.000343 | 3.5329e-07 | 1.6459e-07 | 0.51022
86.85 | 0.674 | 4.203 | 2.02 | 967.118 | 0.000324 | 3.3502e-07 | 1.6581e-07 | 0.62127
91.85 | 0.677 | 4.209 | 1.91 | 963.3911 | 0.000306 | 3.1763e-07 | 1.6696e-07 | 0.75183
96.85 | 0.679 | 4.214 | 1.8 | 960.6148 | 0.000289 | 3.0085e-07 | 1.6774e-07 | 0.90449
100 | 0.68 | 4.217 | 1.76 | 957.8544 | 0.000279 | 2.9128e-07 | 1.6835e-07 | 1.0133
t | k | Cp | Pr | ragua | m | n | a | Psat
ºC | W/(m*K) | kJ/(kg*K) | - | kg/m3 | Pa s | m2/s | m2/s | bar | K
Saturation properties of water as a function of the temperature