## Air Data (hidden)
-73.15 | 0.0181 | 1.007 | 0.737 | 1.7458 | 1.325e-05
-23.15 | 0.0223 | 1.006 | 0.72 | 1.3947 | 1.596e-05
26.85 | 0.0263 | 1.007 | 0.707 | 1.1614 | 1.846e-05
76.85 | 0.03 | 1.009 | 0.7 | 0.995 | 2.082e-05
126.85 | 0.0338 | 1.014 | 0.69 | 0.8711 | 2.301e-05
176.85 | 0.0373 | 1.021 | 0.686 | 0.774 | 2.507e-05
226.85 | 0.0407 | 1.03 | 0.684 | 0.6964 | 2.701e-05
276.85 | 0.0439 | 1.04 | 0.683 | 0.6329 | 2.884e-05
326.85 | 0.0469 | 1.051 | 0.685 | 0.5804 | 3.058e-05
376.85 | 0.0497 | 1.063 | 0.69 | 0.5356 | 3.225e-05
426.85 | 0.0524 | 1.075 | 0.695 | 0.4975 | 3.388e-05
476.85 | 0.0549 | 1.087 | 0.702 | 0.4643 | 3.546e-05
526.85 | 0.0573 | 1.099 | 0.709 | 0.4354 | 3.698e-05
576.85 | 0.0596 | 1.11 | 0.716 | 0.4097 | 3.843e-05
626.85 | 0.062 | 1.121 | 0.72 | 0.3868 | 3.981e-05
676.85 | 0.0643 | 1.131 | 0.723 | 0.3666 | 4.113e-05
726.85 | 0.0667 | 1.141 | 0.726 | 0.3482 | 4.244e-05
t | k | Cp | Pr | ragua | m
ºC | W/(m*K) | kJ/(kg*K) | - | kg/m3 | Pa s
Atmospheric air properties as a function of the temperature
Atmospheric air properties as a function
of the temperature
(Table A.4) | [1]

## Water Data (hidden)
0 | 0.569 | 4.217 | 12.99 | 1000 | 0.00175 | 1.75e-06 | 1.3493e-07 | 0.006108
1.85 | 0.574 | 4.211 | 12.22 | 1000 | 0.001652 | 1.652e-06 | 1.3631e-07 | 0.0069793
6.85 | 0.582 | 4.198 | 10.26 | 1000 | 0.001422 | 1.422e-06 | 1.3864e-07 | 0.0099092
11.85 | 0.59 | 4.189 | 8.81 | 1000 | 0.001225 | 1.225e-06 | 1.4085e-07 | 0.013876
16.85 | 0.598 | 4.184 | 7.56 | 999.001 | 0.00108 | 1.0811e-06 | 1.4307e-07 | 0.019178
21.85 | 0.606 | 4.181 | 6.62 | 998.004 | 0.000959 | 9.6092e-07 | 1.4523e-07 | 0.026181
26.85 | 0.613 | 4.179 | 5.83 | 997.009 | 0.000855 | 8.5756e-07 | 1.4713e-07 | 0.035323
31.85 | 0.62 | 4.178 | 5.2 | 995.0249 | 0.000769 | 7.7284e-07 | 1.4914e-07 | 0.047132
36.85 | 0.628 | 4.178 | 4.62 | 993.0487 | 0.000695 | 6.9986e-07 | 1.5136e-07 | 0.062228
41.85 | 0.634 | 4.179 | 4.16 | 991.0803 | 0.000631 | 6.3668e-07 | 1.5308e-07 | 0.081341
46.85 | 0.64 | 4.18 | 3.77 | 989.1197 | 0.000577 | 5.7758e-07 | 1.5326e-07 | 0.10532
51.85 | 0.645 | 4.182 | 3.42 | 987.1668 | 0.000528 | 5.3486e-07 | 1.5624e-07 | 0.13513
56.85 | 0.651 | 4.184 | 3.15 | 984.252 | 0.000489 | 4.9682e-07 | 1.5784e-07 | 0.1719
61.85 | 0.656 | 4.186 | 2.88 | 982.3183 | 0.000453 | 4.6115e-07 | 1.5953e-07 | 0.21689
66.85 | 0.66 | 4.188 | 2.66 | 979.4319 | 0.00042 | 4.2882e-07 | 1.609e-07 | 0.27153
71.85 | 0.664 | 4.191 | 2.45 | 976.5625 | 0.000389 | 3.9834e-07 | 1.6321e-07 | 0.33742
76.85 | 0.668 | 4.195 | 2.29 | 973.7098 | 0.000365 | 3.7485e-07 | 1.6354e-07 | 0.41632
81.85 | 0.671 | 4.199 | 2.14 | 970.8738 | 0.000343 | 3.5329e-07 | 1.6459e-07 | 0.51022
86.85 | 0.674 | 4.203 | 2.02 | 967.118 | 0.000324 | 3.3502e-07 | 1.6581e-07 | 0.62127
91.85 | 0.677 | 4.209 | 1.91 | 963.3911 | 0.000306 | 3.1763e-07 | 1.6696e-07 | 0.75183
96.85 | 0.679 | 4.214 | 1.8 | 960.6148 | 0.000289 | 3.0085e-07 | 1.6774e-07 | 0.90449
100 | 0.68 | 4.217 | 1.76 | 957.8544 | 0.000279 | 2.9128e-07 | 1.6835e-07 | 1.0133
t | k | Cp | Pr | ragua | m | n | a | Psat
ºC | W/(m*K) | kJ/(kg*K) | - | kg/m3 | Pa s | m2/s | m2/s | bar
Saturation properties of water as a function of the temperature
Saturated Water Properties as a Function
of Temperature (Table A.6) |  | [11]

## 6.CS_Imp (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2
3 | Pipe Thickness [mm], according ASME B36.10M
4
5 | [6 empty] | ASME B36.10M SCHEDULE / IDENTIFICATION | [9 empty] | Application |  | Dn = | 24 | mm
6 | Size | dext | 5 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | STD | XS | XXS | (with input validation) |  | SCH = | XS
7 | 0.5 | 21.3 | 1.65 | 2.11 | - | 2.41 | 2.77 | - | 3.73 | - | 0 | - | 4.78 | 2.77 | 3.73 | 7.47 | di = | Pipe_Imp_CS_Dint_dn_sch |  | #NAME? | mm
8 | 0.75 | 26.7 | 1.65 | 2.11 | - | 2.41 | 2.87 | - | 3.91 | - | 0 | - | 5.56 | 2.87 | 3.91 | 7.82 | de = | Pipe_Imp_CS_Dext_dn |  | #NAME? | mm
9 | 1 | 33.4 | 1.65 | 2.77 | - | 2.9 | 3.38 | - | 4.55 | - | 0 | - | 6.35 | 3.38 | 4.55 | 9.09 | s = | Pipe_Imp_CS_Thickness_dn_sch |  | #NAME? | mm
10 | 1.5 | 48.3 | 1.65 | 2.77 | - | 3.18 | 3.68 | - | 5.08 | - | 0 | - | 7.14 | 3.68 | 5.08 | 10.15
11 | 2 | 60.3 | 1.65 | 2.77 | - | 3.18 | 3.91 | - | 5.54 | - | 0 | - | 8.74 | 3.91 | 5.54 | 11.07 | Application |  | Dn = | 16 | mm
12 | 3 | 88.9 | 2.11 | 3.05 | - | 4.78 | 5.49 | - | 7.62 | - | 0 | - | 11.13 | 5.49 | 7.62 | 15.24 | (without input validation) |  | SCH = | 81
13 | 4 | 114.3 | 2.11 | 3.05 | - | 4.78 | 6.02 | - | 8.56 | - | 11.13 | - | 13.49 | 6.02 | 8.56 | 17.12 | di = | Pipe_Imp_CS_Dint_dn_sch |  | #NAME? | mm
14 | 5 | 141.3 | 2.77 | 3.4 | - | - | 6.55 | - | 9.53 | - | 12.7 | - | 15.88 | 6.55 | 9.53 | 19.05 | de = | Pipe_Imp_CS_Dext_dn |  | #NAME? | mm
15 | 6 | 168.3 | 2.77 | 3.4 | - | - | 7.11 | - | 10.97 | - | 14.27 | - | 18.26 | 7.11 | 10.97 | 21.95 | s = | Pipe_Imp_CS_Thickness_dn_sch |  | #NAME? | mm
16 | 8 | 219.1 | 2.77 | 3.76 | 6.35 | 7.04 | 8.18 | 10.31 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01 | 8.18 | 12.7 | 22.23 | The shedule entered is wrong
17 | 10 | 273 | 3.4 | 4.19 | 6.35 | 7.8 | 9.27 | 12.7 | 15.09 | 18.26 | 21.44 | 25.4 | 28.58 | 9.27 | 12.7 | 25.4
18 | 12 | 323.8 | 3.96 | 4.57 | 6.35 | 8.38 | 10.31 | 14.27 | 17.48 | 21.44 | 25.4 | 28.58 | 33.32 | 9.53 | 12.7 | 25.4
19 | 14 | 355.6 | 3.96 | 6.35 | 7.92 | 9.53 | 11.13 | 15.09 | 19.05 | 23.83 | 27.79 | 31.75 | 35.71 | 9.53 | 12.7 | -
20 | 16 | 406.4 | 4.19 | 6.35 | 7.92 | 9.53 | 12.7 | 16.66 | 21.44 | 26.19 | 30.96 | 36.53 | 40.49 | 9.53 | 12.7 | -
21 | 18 | 457 | 4.19 | 6.35 | 7.92 | 11.13 | 14.27 | 19.05 | 23.83 | 29.36 | 34.93 | 39.67 | 45.24 | 9.53 | 12.7 | -
22 | 20 | 508 | 4.78 | 6.35 | 9.53 | 12.7 | 15.09 | 20.62 | 26.19 | 32.54 | 38.1 | 44.45 | 50.01 | 9.53 | 12.7 | -
23 | 22 | 559 | 4.78 | 6.35 | 9.53 | 12.7 | - | 22.23 | 28.58 | 34.93 | 41.28 | 47.63 | 53.98 | 9.53 | 12.7 | -
24 | 24 | 610 | 5.54 | 6.35 | 9.53 | 14.27 | 17.48 | 24.61 | 30.96 | 38.89 | 46.02 | 52.37 | 59.54 | 9.53 | 12.7 | -
25 | 26 | 660 | - | 7.92 | 12.7 | 15.88 | - | - | - | - | - | - | - | 9.53 | 12.7 | -
26 | 28 | 711 | - | 7.92 | 12.7 | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
27 | 30 | 762 | 6.35 | 7.92 | 12.7 | 15.88 | - | - | - | - | - | - | - | 9.53 | 12.7 | -
28 | 32 | 813 | - | 7.92 | 12.7 | 15.88 | 17.48 | - | - | - | - | - | - | 9.53 | 12.7 | -
29 | 34 | 864 | - | 7.92 | 12.7 | 15.88 | 17.48 | - | - | - | - | - | - | 9.53 | 12.7 | -
30 | 36 | 914 | - | 7.92 | 12.7 | 15.88 | 19.05 | - | - | - | - | - | - | 9.53 | 12.7 | -
31 | 38 | 965 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
32 | 40 | 1016 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
33 | 42 | 1067 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
34 | 44 | 1118 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
35 | 46 | 1168 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
36 | 48 | 1219 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
'PipeImp_CS_Dext_dn
'The function PipeImp_CS_Dext_dn gives the exterior diameter of a pipe with
'nominal diameter dn [in]
'If the diameter is a fraction, the input cell has to be formated as a fraction
Function PipeImp_CS_Dext_dn(Dn)
Dim msg As String
Dim C(36, 3) As Variant
Mensaje = "NO"
' Exterior diameters according ASME B36.10M, from Sheet 6.CS_Imp, 3th column
For m = 1 To 36
C(m, 3) = ThisWorkbook.Worksheets("6.CS_Imp").Cells(m, 3).Value
Next m
' The corresponding line of the matrix C is asigned to its Dn-value
If Dn = 0.5 Then
x = 7
ElseIf Dn = 0.75 Then x = 8
ElseIf Dn = 1 Then x = 9
ElseIf Dn = 1.5 Then x = 10
ElseIf Dn = 2 Then x = 11
ElseIf Dn = 3 Then x = 12
ElseIf Dn = 4 Then x = 13
ElseIf Dn = 5 Then x = 14
ElseIf Dn = 6 Then x = 15
ElseIf Dn = 8 Then x = 16
ElseIf Dn = 10 Then x = 17
ElseIf Dn = 12 Then x = 18
ElseIf Dn = 14 Then x = 19
ElseIf Dn = 16 Then x = 20
ElseIf Dn = 18 Then x = 21
ElseIf Dn = 20 Then x = 22
ElseIf Dn = 22 Then x = 23
ElseIf Dn = 24 Then x = 24
ElseIf Dn = 26 Then x = 26
ElseIf Dn = 28 Then x = 26
ElseIf Dn = 30 Then x = 27
ElseIf Dn = 32 Then x = 28
ElseIf Dn = 34 Then x = 29
ElseIf Dn = 36 Then x = 30
ElseIf Dn = 38 Then x = 31
ElseIf Dn = 40 Then x = 32
ElseIf Dn = 42 Then x = 33
ElseIf Dn = 44 Then x = 34
ElseIf Dn = 46 Then x = 35
ElseIf Dn = 48 Then x = 36
' If the Dn-value is not within the given values,
' The function returns Dext = "N/A"
Else
PipeImp_CS_Dext_dn = "N/A"
Exit Function
End If
' In case the input value for Dn was identified and therefore an x-value "x" has been defined,
' the value of the matrix element (x,3) is assigned to de exterior diameter Dext
PipeImp_CS_Dext_dn = C(x, 3)
End Function
'PipeImp_CS_Thickness_dn_sch
'The function PipeImp_CS_Thickness_dn_sch gives the thickness of a pipe with
'nominal diameter dn [in] and schedule sch
'If the diameter is a fraction, the input cell ha to be formated as a fraction
Function PipeImp_CS_Thickness_dn_sch(Dn, SCH)
Dim C(36, 17) As Variant
' Thickness according ASME B36.10M, from Sheet 6.CS_Imp
For m = 1 To 36
For j = 1 To 17
C(m, j) = ThisWorkbook.Worksheets("6.CS_Imp").Cells(m, j).Value
Next j
Next m
If PipeImp_CS_Dext_dn(Dn) = "N/A" Then
PipeImp_CS_Thickness_dn_sch = "N/A"
Exit Function
End If
If Dn = 0.5 Then
x = 7
ElseIf Dn = 0.75 Then x = 8
ElseIf Dn = 1 Then x = 9
ElseIf Dn = 1.5 Then x = 10
ElseIf Dn = 2 Then x = 11
ElseIf Dn = 3 Then x = 12
ElseIf Dn = 4 Then x = 13
ElseIf Dn = 5 Then x = 14
ElseIf Dn = 6 Then x = 15
ElseIf Dn = 8 Then x = 16
ElseIf Dn = 10 Then x = 17
ElseIf Dn = 12 Then x = 18
ElseIf Dn = 14 Then x = 19
ElseIf Dn = 16 Then x = 20
ElseIf Dn = 18 Then x = 21
ElseIf Dn = 20 Then x = 22
ElseIf Dn = 22 Then x = 23
ElseIf Dn = 24 Then x = 24
ElseIf Dn = 26 Then x = 26
ElseIf Dn = 28 Then x = 26
ElseIf Dn = 30 Then x = 27
ElseIf Dn = 32 Then x = 28
ElseIf Dn = 34 Then x = 29
ElseIf Dn = 36 Then x = 30
ElseIf Dn = 38 Then x = 31
ElseIf Dn = 40 Then x = 32
ElseIf Dn = 42 Then x = 33
ElseIf Dn = 44 Then x = 34
ElseIf Dn = 46 Then x = 35
ElseIf Dn = 48 Then x = 36
Else
PipeImp_CS_Thickness_dn_sch(Dn, SCH) = "N/A"
Exit Function
End If
If SCH = 5 Then
Y = 4
ElseIf SCH = 10 Then Y = 5
ElseIf SCH = 20 Then Y = 6
ElseIf SCH = 30 Then Y = 7
ElseIf SCH = 40 Then Y = 8
ElseIf SCH = 60 Then Y = 9
ElseIf SCH = 80 Then Y = 10
ElseIf SCH = 100 Then Y = 11
ElseIf SCH = 120 Then Y = 12
ElseIf SCH = 140 Then Y = 13
ElseIf SCH = 160 Then Y = 14
ElseIf SCH = "STD" Then Y = 15
ElseIf SCH = "XS" Then Y = 16
ElseIf SCH = "XXS" Then Y = 17
Else
PipeImp_CS_Thickness_dn_sch = "N/A"
Exit Function
End If
PipeImp_CS_Thickness_dn_sch = C(x, Y)
If PipeImp_CS_Thickness_dn_sch = " - " Then
PipeImp_CS_Thickness_dn_sch = "N/A"
End If
End Function
'PipeImp_CS_Dint_dn_sch
'The function PipeImp_CS_Dint_dn_sch gives the interior diameter of a pipe with
'nominal diameter dn [in] and schedule sch
'If the diameter is a fraction, the input cell ha to be formated as a fraction
Function PipeImp_CS_Dint_dn_sch(Dn, SCH)
If PipeImp_CS_Thickness_dn_sch(Dn, SCH) = "N/A" Then
PipeImp_CS_Dint_dn_sch = "N/A"
Exit Function
End If
If PipeImp_CS_Dext_dn(Dn) = "N/A" Then
PipeImp_CS_Dint_dn_sch = "N/A"
Exit Function
End If
PipeImp_CS_Dint_dn_sch = PipeImp_CS_Dext_dn(Dn) - PipeImp_CS_Thickness_dn_sch(Dn, SCH) * 2
End Function

## Index
Rev. cjc. 11.07.2016
Orifice plates dimensioning
1 | O.P. Air | Orifice plate, application for air
2 | O.P. Water, beta < 0.3 | Orifice plate, application for "water" and b < 0.3 | See note
3 | O.P. Water, beta > 0.3 | Orifice plate, application for "water" and b > 0.3 | See note
4 | On-line O.P. calculation | Orifice plate, application using the On-line program "Flowmeter"
5 | Cameron | Orifice plates dimensionig for water, according Cameron
Note
The requirement for a value of b , is only to compare the result with the Cameron equations

## 1. O.P Air
Rev. cjc. 11.07.2016
Page 1 of 3
Orifice plate, application for Air [1] & [3]
Fluid: | Air |  | Tap types (Note 1) |  |  |  | Air properties |  |  | O/P inlet velocity |  |  |  | Note 1
Temperatura |  |  | La= | 0 |  |  | Absolute viscosity |  |  | vin = | Q / A |  |  | La and Lb are functions of tap type
t = | 10 | ºC | Lb = | 0 |  |  | t = | 10 | ºC | Q = | 0.062524 | m³/s |  | Corner taps: La and Lb = 0
Adiabatic exponent | [6 empty] | m = | AirAbsoluteViscosity_t |  | A = | 0.00046377 | m² |  | D & D/2 taps. La and Lb = 0.47
k = | 1.4 | - | Calculation |  |  |  | m = | 1.7617e-05 | Pa s | vin = | 134.8179 | m/s |  | 1" taps. La and Lb = 0.0254 /D
Air constant |  |  | Assumed flow rate (Note 2 ) | [10 empty] | with D (m). For more information, see
R = | 287 | J/(kg*K) | Qass = | 225.0881 | m³/h |  | Inlet density |  |  | Inlet Reynolds number |  |  |  | page 3.
Inlet presure |  |  | Qass = | 0.062524 | m³/s |  | rin = | Pin / ( R * T) |  | Re = | v * d / n
Pin = | 170263 | Pa |  |  |  |  | Pin = | 170263 | Pa | v = | 134.8179 | m/s |  | Note 2
Pressure difference |  |  | Orifice plate section area |  |  |  | R = | 287 | J/(kg*K) | dOP = | 0.0243 | m |  | Assumed flow required for the calculation,
DP = | 68938 | Pa | A = | (p/4) * dOP^2 |  |  | T = | 283.15 | K | n = | 8.4086e-06 | m²/s |  | which can have any positive value.
Dischatge pressure |  |  | dOP = | 0.0243 | m² |  | rin = | 2.0952 | kg/m³ | Re = | 389611.2585 |  |  | As an example, you can leave the existing
Pout = | 101325 | Pa | A = | 0.00046377 | m² | [8 empty] | value in the cell.
Inside pipe diameter | [6 empty] | Kinematic viscosity |  |  | Diameters ratio "b"
dpipe = | 600 | mm |  |  |  |  | n = | m / r |  | b = | dOP / dpipe
Orifice plate diameter | [6 empty] | m = | 1.7617e-05 | Pa s | dOP = | 24.3 | mm
dOP = | 24.3 | mm |  |  |  |  | rin = | 2.0952 | kg/m³ | dpipe = | 600 | mm
dOP = | 0.0243 | m |  |  |  |  | n = | 8.4086e-06 | m²/s | b = | 0.0405 | -
Page 2 of 3
Expansion coefficient "e" |  |  | Orifice plate flowrate
e = 1 - (0.41 + 0.35 * b^4 ) * ( DP/ (k * Pin) )
b = | 0.0405 | - |  |  |  |  | Iteration routine
DP = | 68938 | Pa |  |  |  |  | DQ = | Qass - Q
k = | 1.4 | - |  |  |  |  | Qass = | 225.0881 | m³/h
Pin = | 170263 | Pa |  |  |  |  | Qcalc = | 225.0881 | m³/h
e = | 0.88142 | - | Qcalc = | C * e * E * A * (2 * DP/ rin)^0.5 |  |  | DQ = | -1.6719e-07 | m³/h
|  |  | C = | 0.59625 | -
Discharge coefficient "C" |  |  | e = | 0.88142 | -
Equation (1) |  |  | E = | 1 | - |  | Iteration finished
La= | 0 | - | A = | 0.00046377 | m²
Lb = | 0 | - | DP = | 68938 | Pa
Re | 389611.2585 | - | rin = | 2.0952 | kg/m³ |  | Calculated result
e = | 0.88142 | - | Q = | 0.062524 | m³/s |  | Orifice plate flow rate
C = | 0.59625 |  | Qcalc = | 225.0881 | m³/h |  | Q = | 225.0881 | m³/h
"E" value
E = | ( 1 / (1 - b^4) )^0.5
b = | 0.0405 | -
E = | 1 | -
Equation (1)
C = 0.5961 + 0.0261*b^2 - 0.216 * b^8 + 0.000521 * (b*1e67Re)^0.7 + ( 0.0188 + 0.0063 *(19000*b/Re)0.8 ) * ( 1e6/Re ) * b^3.5 + ( 0.043 + 0.08*e^(-7*La) ) * ( 1-0.11 ) * (19000*b)/Re)^0.8 * ( b^4/(1-b^4) ) - 0.031 * ((2*Lb/(1-b)) - 0.8*(2*Lb/(1-b))^1.1)*b^1.3
Page 3 of 3
Q: Flowrate |  |  | [m3/s]
C: Dischatge coefficient |  |  | [-] | C = f(b, Re, e, La, Lb) |  | Ec. 1
e: Expansion coefficient |  |  | [-] | e = 1 - (0.41 + 0.35 * b^4 ) * ( DP/ (k * Pin) )
e = 1 for incompressible fluids
E: E- value |  |  | [-] | E = ( 1 / (1 - b^4) )^0.5
A: O/P area |  |  | [m²] | A = (p/4) * d^2
DP : Pressure diferential |  |  | [Pa] | DP = Pin - Pout
r: Fluid density |  |  | [kg/m3]
k: adiabtic exponent |  |  | [-]
(Not required for incompresible fluids)
dOP: O/P diameter |  |  | [mm]
dpipe: Pipe diameter |  |  | [mm]
b: Diameter ratio |  |  | b = dOP/dpipe
La y Lb: Constants depending on
tapping type
[11 empty] | g = | 9.8066 | m/s²
Equation (1)
C = 0.5961 + 0.0261*b^2 - 0.216 * b^8 + 0.000521 * (b*1e67Re)^0.7 + ( 0.0188 + 0.0063 *(19000*b/Re)0.8 ) * ( 1e6/Re ) * b^3.5 + ( 0.043 + 0.08*e^(-7*La) ) * ( 1-0.11 ) * (19000*b)/Re)^0.8 * ( b^4/(1-b^4) ) - 0.031 * ((2*Lb/(1-b)) - 0.8*(2*Lb/(1-b))^1.1)*b^1.3

## 2. O.P. Water, beta < 0.3
Rev. cjc. 11.07.2016
Page 1 of 3
Orifice plate (O/P), application for "water" and b < 0.3 [1] & [3]
The requirement b < 0.3, is only to compare the result with the Cameron equation for an O/P with b < 0.3
Fluid: | Water
Temperature |  |  | Tap types (Note 1) |  |  |  | Water properties |  |  | O/P inlet velocity |  |  |  | Note 1
t = | 10 | ºC | La= | 0 |  |  | Absolute viscosity |  |  | vin = | Q / A |  |  | La and Lb are functions of tap type
O/P inlet pressure |  |  | Lb = | 0 |  |  | t = | 10 | ºC | Q = | 0.003249 | m³/s |  | Corner taps: La and Lb = 0
Pin = | 170372 | Pa |  |  |  |  | m = | AirAbsoluteViscosity_t |  | A = | 0.00046377 | m² |  | D & D/2 taps. La and Lb = 0.47
O/P outlet pressure |  |  | Orifice plate section area |  |  |  | m = | 1.7617e-05 | Pa s | vin = | 7.0056 | m/s |  | 1" taps. La and Lb = 0.0254 /D
Pout = | 101325 | Pa | A = | 0.00046377 | m² | [8 empty] | with D (m). For more information, see
Pressure difference | [6 empty] | Inlet density |  |  | Inlet Reynolds number |  |  |  | page 3.
DP = | 69047 | Pa | Calculation |  |  |  | rin = | f(t, p) |  | Re = | v * d / n
Inside pipe diameter |  |  | Assumed flow rate (Note 2 ) |  |  |  | t = | 10 | °C | v = | 7.0056 | m/s |  | Note 2
dpipe = | 600 | mm | Qass = | 11.6964 | m³/h |  | p = | 1.7037 | bar | dOP = | 0.0243 | m |  | Assumed flow required for the calculation,
Orifice plate diameter |  |  | Qass = | 0.003249 | m³/s |  | rin = | SaturatedWaterDensity_t |  | n = | 1.7617e-08 | m²/s |  | which can have any positive value.
dOP = | 24.3 | mm |  |  |  |  | rin = | 1000 | kg/m³ | Re = | 9662922.4534 |  |  | As an example, you can leave the existing
dOP = | 0.0243 | m | [11 empty] | value in the cell.
[7 empty] | Kinematic viscosity |  |  | Diameters ratio "b"
[7 empty] | n = | m / r |  | b = | dOP / dpipe
[7 empty] | m = | 1.7617e-05 | Pa s | dOP = | 24.3 | mm
[7 empty] | r = | 1000 | kg/m3 | dpipe = | 600 | mm
[7 empty] | n = | 1.7617e-08 | m²/s | b = | 0.0405 | -
Page 2 of 3
Expansion coefficient "e" |  |  | Orifice plate flow rate
e = 1 for incompressible fluids | [9 empty] | Cameron
e = | 1 | - |  |  |  |  | Iteration routine |  |  | Checking with Cameron`s [2]equation
[7 empty] | DQ = | Qass - Q |  | applicable for water and b < 0.3
[7 empty] | Qass = | 11.6964 | m³/h
Discharge coefficient "C" | [6 empty] | Qcalc = | 11.6964 | m³/h |  |  |  | (1)
(See Eq. 1) |  |  | Qcalc = | C * e * E * A * (2 * DP/ rin)^0.5 |  |  | DQ = | -1.1006e-06 | m³/h
La= | 0 | - | C = | 0.59615 | - |  |  |  |  | Q = | 0,01252* C * d^2 *( h)^0,5
Lb = | 0 | - | e = | 1 | - |  |  |  |  | valid for b = d/Di < 0,3
Re | 9662922.4534 | - | E = | 1 | - |  | Iteration finished
e = | 1 | - | A = | 0.00046377 | m² |  |  |  |  | b = | 0.0405 | OK. Beta < 0.3
C = | 0.59615 |  | DP = | 69047 | Pa |  |  |  |  | C = | 0.61 | - (constant)
|  |  | rin = | 1000 | kg/m³ |  | Calculation result |  |  | d = | 24.3 | mm
E-value |  |  | Q = | 0.003249 | m³/s |  | Orifice plate flow rate |  |  | h = | 7.0408 | m
E = | ( 1 / (1 - b^4) )^0.5 |  | Qcalc = | 11.6964 | m³/h |  | Q = | 11.6964 | m³/h | Q = | 11.9663 | m³/h
b = | 0.0405 | -
E = | 1 | -
Eq. 1
C = 0.5961 + 0.0261*b^2 - 0.216 * b^8 + 0.000521 * (b*1e67Re)^0.7 + ( 0.0188 + 0.0063 *(19000*b/Re)0.8 ) * ( 1e6/Re ) * b^3.5 + ( 0.043 + 0.08*e^(-7*La) ) * ( 1-0.11 ) * (19000*b)/Re)^0.8 * ( b^4/(1-b^4) ) - 0.031 * ((2*Lb/(1-b)) - 0.8*(2*Lb/(1-b))^1.1)*b^1.3
Page 3 of 3
Q: Flow rate |  |  | [m3/s]
C: Discharge coefficient |  |  | [-] | C = f(b, Re, e, La, Lb) |  | Ec. 1
e: Expansion coefficient |  |  | [-] | e = 1 - (0.41 + 0.35 * b^4 ) * ( DP/ (k * Pin) )
e = 1 for incmpressible fluids
E: "E" value |  |  | [-] | E = ( 1 / (1 - b^4) )^0.5
A: O/P area |  |  | [m²] | A = (p/4) * d^2
DP : Pressure diferential |  |  | [Pa] | DP = Pin - Pout
r: Fluid density |  |  | [kg/m3]
k: adiabtic exponent |  |  | [-]
(Not required for incompresible fkuids)
dOP: O/P diameter |  |  | [mm]
dpipe: Pipe diameter |  |  | [mm]
b: Diameter ratio |  |  | b = dOP/dpipe
La y Lb: Constants depending on
tapping type
Equation (1)
C = 0.5961 + 0.0261*b^2 - 0.216 * b^8 + 0.000521 * (b*1e67Re)^0.7 + ( 0.0188 + 0.0063 *(19000*b/Re)0.8 ) * ( 1e6/Re ) * b^3.5 + ( 0.043 + 0.08*e^(-7*La) ) * ( 1-0.11 ) * (19000*b)/Re)^0.8 * ( b^4/(1-b^4) ) - 0.031 * ((2*Lb/(1-b)) - 0.8*(2*Lb/(1-b))^1.1)*b^1.3

## 3. O.P. Water, beta > 0.3
Rev. cjc. 11.07.2016
Orifice plate (O/P), application for "water" and b > 0.3 [1]
The requirement b > 0.3, is only to compare the result with the Cameron equation for an O/P with b > 0.3
Fluio: | Water |  | Tap types (Note 1) |  |  |  | Water properties |  |  | O/P inlet velocity |  |  |  | Note 1
Temperature |  |  | La= | 0 |  |  | Absolute viscosity |  |  | vin = | Q / A |  |  | La and Lb are functions of tap type
t = | 10 | ºC | Lb = | 0 |  |  | t = | 10 | ºC | Q = | 0.0033025 | m³/s |  | Corner taps: La and Lb = 0
O/P inlet pressure | [6 empty] | m = | SaturWater_DynViscosity_t |  | A = | 0.00046377 | m² |  | D & D/2 taps. La and Lb = 0.47
Pin = | 170372 | Pa | Area |  |  |  | m = | 0.0012979 | Pa s | vin = | 7.121 | m/s |  | 1" taps. La and Lb = 0.0254 /D
P/O outlet pressure |  |  | A = | 0.00046377 | m² | [8 empty] | with D (m). For more information, see
Pout = | 101325 | Pa |  |  |  |  | Inlet density |  |  | Inlet Reynolds number |  |  |  | page 3.
Pressure difference |  |  | Calculation |  |  |  | rin = | f(t, p) |  | Re = | v * d / n
DP = | 69047 | Pa | Assumed flow rate (Note 2 ) |  |  |  | t = | 10 | °C | v = | 7.121 | m/s |  | Note 2
Inside pipe diameter |  |  | Qas = | 11.8891 | m³/h |  | p = | 1.7037 | bar | dOP = | 0.0243 | m |  | Assumed flow required for the calculation,
dpipe = | 75 | mm | Qass = | 0.0033025 | m³/s |  | rin = | SaturatedWaterDensity_t |  | n = | 1.2979e-06 | m²/s |  | which can have any positive value.
O/P diameter | [6 empty] | rin = | 1000 | kg/m³ | Re = | 133324.9603 |  |  | As an example, you can leave the existing
dOP = | 24.3 | mm | [11 empty] | value in the cell.
dOP = | 0.0243 | m |  |  |  |  | Kinematic viscosity |  |  | Diameters ratio "b"
[7 empty] | n = | m / r |  | b = | dOP / dpipe
[7 empty] | m = | 0.0012979 | Pa s | dOP = | 24.3 | mm
[7 empty] | r = | 1000 | kg/m3 | dpipe = | 75 | mm
[7 empty] | n = | 1.2979e-06 | m²/s | b = | 0.324 | -
Expansion coefficient "e" |  |  | Orifice plate flow rate
e = 1 for incompressible fluids | [9 empty] | Cameron
e = | 1 | - |  |  |  |  | Iteration routine |  |  | Checking with Cameron`s[2] equation
[7 empty] | DQ = | Qass - Q |  | applicable for water and b > 0.3
Discharge coefficient "C" | [6 empty] | Qass = | 11.8891 | m³/h
(See Eq. 1) | [6 empty] | Qcalc = | 11.8891 | m³/h |  |  |  |  | (2)
La= | 0 | - | Q = | C * e * E * A * (2 * DP/ rin)^0.5 |  |  | DQ = | -5.3696e-10 | m³/h
Lb = | 0 | - | C = | 0.60263 | - |  |  |  |  | Q = | A * C * d^2 * h^0.5 * (1/(1-b^4))^0.5
Re | 133324.9603 | - | e = | 1 | - |  |  |  |  | with b = d/Di >0,3
e = | 1 | - | E = | 1.0056 | - |  | Iteration finished |  |  | A = | 0.0034781 | - | - (constant)
C = | 0.60263 |  | A = | 0.00046377 | m² |  |  |  |  | C = | 0.61 | - | - (constant)
|  |  | DP = | 69047 | Pa |  |  |  |  | d = | 24.3 | mm
E-value |  |  | rin = | 1000 | kg/m³ |  | Calculated result |  |  | h = | 7.0408 | mca
E = | ( 1 / (1 - b^4) )^0.5 |  | Q = | 0.0033025 | m³/s |  | Orifice plate flow rate |  |  | D = | 75 | mm
b = | 0.324 | - | Q = | 11.8891 | m³/h |  | Q = | 11.8891 | m³/h | b = | d/D
E = | 1.0056 | - | [7 empty] | b = | 0.324 | OK. Beta > 0.3
[10 empty] | Q = | 3.3427 | l/s
[10 empty] | Q = | 12.0339 | m³/h
Ec. 1
C = 0.5961 + 0.0261*b^2 - 0.216 * b^8 + 0.000521 * (b*1e67Re)^0.7 + ( 0.0188 + 0.0063 *(19000*b/Re)0.8 ) * ( 1e6/Re ) * b^3.5 + ( 0.043 + 0.08*e^(-7*La) ) * ( 1-0.11 ) * (19000*b)/Re)^0.8 * ( b^4/(1-b^4) ) - 0.031 * ((2*Lb/(1-b)) - 0.8*(2*Lb/(1-b))^1.1)*b^1.3
Eq. 1
C = 0.5961 + 0.0261*b^2 - 0.216 * b^8 + 0.000521 * (b*1e67Re)^0.7 + ( 0.0188 + 0.0063 *(19000*b/Re)0.8 ) * ( 1e6/Re ) * b^3.5 + ( 0.043 + 0.08*e^(-7*La) ) * ( 1-0.11 ) * (19000*b)/Re)^0.8 * ( b^4/(1-b^4) ) - 0.031 * ((2*Lb/(1-b)) - 0.8*(2*Lb/(1-b))^1.1)*b^1.3
Q: Flow rate |  |  | [m3/s]
C: Coeficiente de decarga. |  |  | [-] | C = f(b, Re, e, La, Lb) |  | Ec. 1
e: Coeficiente de expansión. |  |  | [-] | e = 1 - (0.41 + 0.35 * b^4 ) * ( DP/ (k * Pin) )
e = 1 para fluidos incompresibles
E: Función de diámetros |  |  | [-] | E = ( 1 / (1 - b^4) )^0.5
A: Area de la sección del orificio |  |  | [m²] | A = (p/4) * d^2
DP : Diferencia de presión |  |  | [Pa] | DP = Pin - Pout
r: Densidad del fluido |  |  | [kg/m3]
k: Razón de calores específicos |  |  | [-]
(No se requiere para fluidos incompresibles
dOP: Diámetro del orificio |  |  | [mm]
dpipe: Diámetro de la cañería |  |  | [mm]
b: Razón de diámetros |  |  | b = dOP/dpipe
La y Lb: Constantes dpendientes
del tipo de tapping

## 4. On-line OP calc.
http://www.flowmeterdirectory.com/flowmeter_orifice_calc.html | [1] | Rev. cjc. 11.07.2016
Orifice plate, application using a On-line program "Flowmeter" |  |  | Fluid: | Air |  | O/P inlet velocity
|  |  | Temperatura |  |  | vin = | 134.8179 | m/s
|  |  | t = | 10 | ºC | Inlet Reynolds number
|  |  | Adiabatic exponent |  |  | Re = | 389611.2585
|  |  | k = | 1.4 | - | Diameters ratio "b"
|  |  | Air constant |  |  | b = | 0.0405 | -
|  |  | R = | 287 | J/(kg*K) | Expansion coefficient "e"
|  |  | Inlet presure |  |  | e = | 0.88142 | -
|  |  | Pin = | 170263 | Pa | Discharge coefficient "C"
|  |  | Pressure difference |  |  | C = | 0.59625
|  |  | DP = | 68938 | Pa | "E" value
|  |  | Dischatge pressure |  |  | E = | 1 | -
|  |  | Pout = | 101325 | Pa
Inside pipe diameter
|  |  | dpipe = | 600 | mm | Qcalc = | C * e * E * A * (2 * DP/ rin)^0.5
|  |  | Orifice plate diameter |  |  | Qcalc = | 225.0881 | m³/h
|  |  | dOP = | 24.3 | mm
|  |  | dOP = | 0.0243 | m
Air properties
Absolute viscosity
|  |  | t = | 10 | ºC
|  |  | m = | AirAbsoluteViscosity_t
|  |  | m = | 1.7617e-05 | Pa s
Inlet density
|  |  | rin = | Pin / ( R * T) | c
|  |  | Pin = | 170263 | Pa
|  |  | R = | 287 | J/(kg*K)
|  |  | T = | 273.15 | K
|  |  | rin = | 2.1719 | kg/m³
Kinematic viscosity
|  |  | n = | m / r
|  |  | m = | 1.7617e-05 | Pa s
|  |  | rin = | 2.1719 | kg/m³
|  |  | n = | 8.1116e-06 | m²/s
Coefficient of discharge ISO equation
C = 0.5961 + 0.0261*c96^2 - 0.216 * c96^8 + 0.000521 * (c96*1e67Re)^0.7 + ( 0.0188 + 0.0063 *(19000*c96/Re)0.8 ) * ( 1e6/Re ) * c96^3.5 + ( 0.043 + 0.08*e^(-7*La) ) * ( 1-0.11 ) * (19000*c96)/Re)^0.8 * ( c96^4/(1-c96^4) ) - 0.031 * ((2*Lc96/(1-c96)) - 0.8*(2*Lc96/(1-c96))^1.1)*c96^1.3

## 5. Cameron
| Orifice plates dimensionig for water, according Cameron [2] | [6 empty] | Rev. cjc. 11.07.2016
Orifice plate for water and diameters ratio b < 0.3
| Orifice plate water flowrate for b < 0.3 |  |  |  | Pressure loss in orifice plate, for
water and b < 0.3
Equation adapted from Cameron [3], pag. 2-8
From Eq. 1
[Ec. 1]
| Q: volumetric flowrate [m3/h] |  |  |  | Q: volumetric flowrate [m3/h]
| C: discharge coefficient [-] |  |  |  | C: discharge coefficient [-]
| d: orifice plate diameter [mm] |  |  |  | d: orifice plate diameter [mm]
| h: orifice plate pressure difference [m] |  |  |  | h: orifice plate pressure difference [m]
| Application for water flowrate calculation |  |  |  | Application for water pressure difference calculation
| for b = d/Di < 0,3 |  |  |  | for b = d/Di < 0,3
| Q = | 0,01252* C * d^2 *( h)^0,5 |  |  | h = | Q^2 / (0,000157*C^2*d^4 )
| C = | 0.61 | - (constant) |  | Q = | 13.0641 | m³/h
| d = | 25.4 | mm |  | C = | 0.61 | - (constant)
| h = | 7.03 | m |  | d = | 25.4 | mm
| Q = | 13.0641 | m³/h |  | h = | 7.0188 | m
Orifice plate for water and diameters ratio b > 0.3
| Orifice plate water flowrate for b > 0.3 |  |  |  | Pressure loss in orifice plate, for
water and b > 0.3
Equation adapted from Cameron [3], pag. 2-8
From Eq. 2
`[Ec. 2]
| Q: volumetric flowrate [m3/h] |  |  |  | Q: volumetric flowrate [m3/h]
| C: discharge coefficient [-] |  |  |  | C: discharge coefficient [-]
| d: orifice plate diameter [mm] |  |  |  | d: orifice plate diameter [mm]
| h: orifice plate pressure difference [m] |  |  |  | h: orifice plate pressure difference [m]
| Application for water flowrate calculation |  |  |  | Application for water pressure difference calculation
presión de un flujo de agua.
| for b = d/Di > 0,3 |  |  |  | for b = d/Di > 0,3
| Q = | A * C * d^2 * h^0.5 * (1/(1-b^4))^0.5 |  |  | h = | (Q / ( A * C * d^2 * (1/(1-b^4))^0,5 ))^2
| A = | 0.0034781 | - |  | Q = | 949 | m³/h
| C = | 0.61 | - (constant) |  | Q = | 263.6111 | l/s
| d = | 149 | mm |  | A = | 0.0034781 | -
| h = | 30.753 | m |  | C = | 0.61 | - (constant)
| D = | 406 | mm |  | d = | 149 | mm
| b = | d/D |  |  | D = | 406 | mm
| b = | 0.367 | ( > 0,3 ) |  | b = | d/D
| Q = | 263.6111 | l/s |  | b = | 0.367 | ( > 0,3 )
| Q = | 949 | m³/h |  | h = | 30.753 | m

## Ref
[1] | FlowRental.com
Orifice plate on-line calculator
http://www.flowmeterdirectory.com/flowmeter_orifice_calc.html
http://www.flowmeterdirectory.com/flowmeter_orifice_calc.html
[2] | Cameron Hydraulic Data, Pag. 2-8