## Resume
rev. cjc. 04.02.2022
| Resume of pipe functions |  |  | Note: For shedules, use capital letters
1 | Carbon steel (dn, Imperial units) |  | Dn = | 0.1 | in | 5 | HDPE PE100 (dn, Imperial units) |  | Dn = | 64 | in
|  |  | SCH = | 80 | - |  |  |  | PN = | 6 | bar
| di = | Pipe_Imp_CS_Dint_dn_sch | di = | N/A | mm |  | di = | Pipe_Imp_HD100_Dint_Dn_PN | di = | 1484.2 | mm
| de = | Pipe_Imp_CS_Dext_dn | de = | N/A | mm |  | de = | Pipe_Imp_HD100_Dext_Dn | de = | 1600 | mm
| s = | Pipe_Imp_CS_Thickness_dn_sch | s = | N/A | mm |  | s = | Pipe_Imp_HD100_Thickness_Dn_PN | s = | 57.9 | mm
2 | Carbon steel (dn, SI units) |  | Dn = | 1200 | mm | 6 | HDPE PE100 (dn, SI units) |  | Dn = | 15 | mm
|  |  | SCH = | XS | - |  |  |  | PN = | 4 | bar
| di = | Pipe_SI_CS_Dint_dn_sch | di = | 1193.8 | mm |  | di = | Pipe_SI_HD100_Dint_Dn_PN | di = | N/A | mm
| de = | Pipe_SI_CS_Dext_dn | de = | 1219.2 | mm |  | de = | Pipe_SI_HD100_Dext_Dn(Dn) | de = | N/A | mm
| s = | Pipe_SI_CS_Thickness_dn_sch | s = | 12.7 | mm |  | s = | Pipe_SI_HD100_Thickness_Dn_PN | s = | N/A | mm
3 | Stainless steel (dn Imperial units) |  | Dn = | 0.125 | in | 7 | HDPE PE80 (dn, Imperial units) |  | Dn = | 64 | in
|  |  | SCH = | 10S | - |  |  |  | PN = | 2.5 | bar
| di = | Pipe_Imp_SS_Dint_Dn_SCH | di = | 7.82 | mm |  | di = | Pipe_Imp_HD80_Dint_Dn_PN | di = | 1521.6 | mm
| de = | Pipe_Imp_SS_Dext_Dn | de = | 10.3 | mm |  | de = | Pipe_Imp_HD80_Dext_Dn | de = | 1600 | mm
| s = | Pipe_Imp_SS_Thickness_Dn_SCH | s = | 1.24 | mm |  | s = | Pipe_Imp_HD80_Thickness_Dn_PN | s = | 39.2 | mm
4 | Stainless steel (dn, SI units) |  | Dn = | 750 | mm | 8 | HDPE PE80 (dn, SI units) |  | Dn = | 1600 | mm
|  |  | SCH = | 10S | - |  |  |  | PN = | 3.2 | bar
| di = | Pipe_SI_SS_Dint_dn_sch | di = | 746.16 | mm |  | di = | Pipe_SI_HD80_Dint_Dn_PN | di = | 1502 | mm
| de = | Pipe_SI_SS_Dext_dn | de = | 762 | mm |  | de = | Pipe_SI_HD80_Dext_Dn | de = | 1600 | mm
| s = | Pipe_SI_SS_Thickness_dn_sch | s = | 7.92 | mm |  | s = | Pipe_SI_HD80_Thickness_Dn_PN | s = | 49 | mm

## Data
[24 empty] | Rev. cjc.10.05.2021 | Old rev. cjc. 07.03.2017
Carbon steel pipes with nominal diameter input dn in milimeters and in inches, exterior diameter and thickness in milimeters, according ASME B36.10M
[25 empty] | Check |  |  | Check
|  |  |  | Carbon steel pipe thickness s (mm) | [15 empty] | Carbon steel (with input validation) |  |  |  |  | Carbon steel pipe SI |  |  | Carbon steel pipe Imp
| dn | dn | dext | ASME B36.10M SCHEDULE | [14 empty] | Imperial |  |  | SI
| mm | " | mm | 5 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | STD | XS | XXS |  | Pipe_Imp_CS_Dext_dn |  |  | Pipe_SI_CS_Dext_dn |  |  | dn = | 25 | mm | dn = | 1 | in
| 6 | 0.125 | 10.3 | 0 | 1.24 | 0 | 1.45 | 1.73 | 0 | 2.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Pipe_Imp_CS_Thickness_dn_sch |  |  | Pipe_SI_CS_Thickness_dn_sch |  |  | Sch = | 80 |  | Sch = | 80
| 8 | 0.25 | 13.7 | 0 | 1.65 | 0 | 1.85 | 2.24 | 0 | 3.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Pipe_Imp_CS_Dint_dn_sch |  |  | Pipe_SI_CS_Dint_dn_sch
| 10 | 0.375 | 17.1 | 0 | 1.65 | 0 | 1.85 | 2.31 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | Dext = | 33.4 | mm | Dext = | 33.4 | in
| 15 | 0.5 | 21.3 | 1.65 | 2.11 | 0 | 2.41 | 2.77 | 0 | 3.73 | 0 | 0 | 0 | 4.78 | 2.77 | 3.73 | 7.47 | [7 empty] | s = | 4.55 | mm | s = | 4.55 | in
| 20 | 0.75 | 26.7 | 1.65 | 2.11 | 0 | 2.41 | 2.87 | 0 | 3.91 | 0 | 0 | 0 | 5.56 | 2.87 | 3.91 | 7.82 |  | dn = | 6 | in | dn = | 20 | mm | Dint = | 24.3 | mm | Dint = | 24.3 | in
| 25 | 1 | 33.4 | 1.65 | 2.77 | 0 | 2.9 | 3.38 | 0 | 4.55 | 0 | 0 | 0 | 6.35 | 3.38 | 4.55 | 9.09 |  | Sch = | 80 |  | Sch = | XXS
| 32 | 1.25 | 42.2 | 1.65 | 2.77 | 0 | 2.97 | 3.56 | 0 | 4.85 | 0 | 0 | 0 | 6.35 | 3.56 | 4.85 | 9.7 | [7 empty] | Input error in nominal diameter |  |  | Input error in nominal diameter
| 40 | 1.5 | 48.3 | 1.65 | 2.77 | 0 | 3.18 | 3.68 | 0 | 5.08 | 0 | 0 | 0 | 7.14 | 3.68 | 5.08 | 10.15 |  | Dext = | 168.3 | mm | Dext = | 26.7 | mm | dn = | 23 | mm | dn = | 20 | in
| 50 | 2 | 60.3 | 1.65 | 2.77 | 0 | 3.18 | 3.91 | 0 | 5.54 | 0 | 0 | 0 | 8.74 | 3.91 | 5.54 | 11.07 |  | s = | 10.97 | mm | s = | 7.82 | mm | Sch = | 80 |  | Sch = | 21
| 65 | 2.5 | 73 | 2.11 | 3.05 | 0 | 4.78 | 5.16 | 0 | 7.01 | 0 | 0 | 0 | 9.53 | 5.16 | 7.01 | 14.02 |  | Dint = | 146.36 | mm | Dint = | 11.06 | mm
| 80 | 3 | 88.9 | 2.11 | 3.05 | 0 | 4.78 | 5.49 | 0 | 7.62 | 0 | 0 | 0 | 11.13 | 5.49 | 7.62 | 15.24 | [7 empty] | Dext = | 33.4 | mm | Dext = | 508 | in
| 90 | 3.5 | 101.6 | 2.11 | 3.05 | 0 | 4.78 | 5.74 | 0 | 8.08 | 0 | 0 | 0 | - | 5.74 | 8.08 | - | [7 empty] | s = | 2.41 | mm | s = | N/A | in
| 100 | 4 | 114.3 | 2.11 | 3.05 | 0 | 4.78 | 6.02 | 0 | 8.56 | 0 | 0 | 0 | 13.49 | 6.02 | 8.56 | 17.12 | [7 empty] | Dint = | 28.58 | mm | Dint = | N/A | in
| 125 | 5 | 141.3 | 2.77 | 3.4 | 0 | 0 | 6.55 | 0 | 9.53 | 0 | 0 | 0 | 15.88 | 6.55 | 9.53 | 19.05
| 150 | 6 | 168.3 | 2.77 | 3.4 | 0 | 0 | 7.11 | 0 | 10.97 | 0 | 0 | 0 | 18.26 | 7.11 | 10.97 | 21.95
| 200 | 8 | 219.1 | 2.77 | 3.76 | 6.35 | 7.04 | 8.18 | 10.31 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01 | 8.18 | 12.7 | 22.23 |  |  | Extracted from carbon steel pipe data |  |  |  |  | Imput error en schedule |  |  | Imput error en schedule
| 250 | 10 | 273 | 3.4 | 4.19 | 6.35 | 7.8 | 9.27 | 12.7 | 15.09 | 18.26 | 21.44 | 25.4 | 28.58 | 9.27 | 12.7 | 25.4 |  |  | from: |  |  |  |  | dn = | 20 | mm | dn = | 0.75 | in
| 300 | 12 | 323.8 | 3.96 | 4.57 | 6.35 | 8.38 | 10.31 | 14.27 | 17.48 | 21.44 | 25.4 | 28.58 | 33.32 | 9.53 | 12.7 | 25.4 |  |  | ASME B36.10M-2000 |  |  |  |  | Sch = | 81 |  | Sch = | 81
| 350 | 14 | 355.6 | 3.96 | 6.35 | 7.92 | 9.53 | 11.13 | 15.09 | 19.05 | 23.83 | 27.79 | 31.75 | 35.71 | 9.53 | 12.7 | 0 |  |  | (Revision of ASME B36.10M-1996)
| 400 | 16 | 406.4 | 4.19 | 6.35 | 7.92 | 9.53 | 12.7 | 16.66 | 21.44 | 26.19 | 30.96 | 36.53 | 40.49 | 9.53 | 12.7 | 0 |  |  | Table 1 Dimensions and weights of |  |  |  |  | Dext = | 26.7 | mm | Dext = | 26.7 | in
| 450 | 18 | 457 | 4.19 | 6.35 | 7.92 | 11.13 | 14.27 | 19.05 | 23.83 | 29.36 | 34.93 | 39.67 | 45.24 | 9.53 | 12.7 | 0 |  |  | welded and seamless wrought steel pipe |  |  |  |  | s = | N/A | mm | s = | N/A | in
| 500 | 20 | 508 | 4.78 | 6.35 | 9.53 | 12.7 | 15.09 | 20.62 | 26.19 | 32.54 | 38.1 | 44.45 | 50.01 | 9.53 | 12.7 | 0 | [7 empty] | Dint = | N/A | mm | Dint = | N/A | in
| 550 | 22 | 559 | 4.78 | 6.35 | 9.53 | 12.7 | 0 | 22.23 | 28.58 | 34.93 | 41.28 | 47.63 | 53.98 | 9.53 | 12.7 | 0
| 600 | 24 | 610 | 5.54 | 6.35 | 9.53 | 14.27 | 17.48 | 24.61 | 30.96 | 38.89 | 46.02 | 52.37 | 59.54 | 9.53 | 12.7 | 0
| 650 | 26 | 660 | 0 | 7.92 | 12.7 | 15.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 700 | 28 | 711 | 0 | 7.92 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 750 | 30 | 762 | 6.35 | 7.92 | 12.7 | 15.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 800 | 32 | 813 | 0 | 7.92 | 12.7 | 15.88 | 17.48 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 850 | 34 | 864 | 0 | 7.92 | 12.7 | 15.88 | 17.48 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 900 | 36 | 914 | 0 | 7.92 | 12.7 | 15.88 | 19.05 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 950 | 38 | 965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 1000 | 40 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 1050 | 42 | 1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 1100 | 44 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 1150 | 46 | 1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
| 1200 | 48 | 1219.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.53 | 12.7 | 0
Stainless steel thickness according ASME B36.19-1985
Nominal diameter in milimeters and in inches
Reference
|  |  |  | Stainless steel pipe thickness s (mm) | [6 empty] | Stainless steel (with input validation) | [8 empty] | Stainless steel pipe
| dn | dn | dext | Schedule | [15 empty] | ANSI/ASME B36.19M-1985
| mm | in | mm | 5S | 10S | 40S | 80S |  |  |  | Imperial |  |  |  |  | SI |  |  |  | Reaffirmed 1994
| 6 | 0.125 | 10.3 | 0 | 1.24 | 1.73 | 2.41 | [12 empty] | Tables 2A. Dimensions of welded and seamless steel pipe - SI units
| 8 | 0.25 | 13.7 | 0 | 1.65 | 2.24 | 3.02 |  |  |  | dn = | 2 | in |  |  | dn = | 100 | mm
| 10 | 0.375 | 17.1 | 0 | 1.65 | 2.31 | 3.2 |  |  |  | Sch = | 40S |  |  |  | Sch = | 40S
| 15 | 0.5 | 21.3 | 1.64 | 2.11 | 2.77 | 3.73
| 20 | 0.75 | 26.7 | 1.65 | 2.11 | 2.87 | 3.91 |  |  |  | Dext = | 60.3 | mm |  |  | Dext = | 114.3 | mm
| 25 | 1 | 33.4 | 1.65 | 2.77 | 3.38 | 4.55 |  |  |  | s = | 3.91 | mm |  |  | s = | 6.02 | mm
| 32 | 1.25 | 42.2 | 1.65 | 2.77 | 3.56 | 4.85 |  |  |  | Dint = | 52.48 | mm |  |  | Dint = | 102.26 | mm
| 40 | 1.5 | 48.3 | 1.65 | 2.77 | 3.68 | 5.08
| 50 | 2 | 60.3 | 1.65 | 2.77 | 3.91 | 5.54
| 65 | 2.5 | 73 | 2.11 | 3.05 | 5.16 | 7.01
| 80 | 3 | 88.9 | 2.11 | 3.05 | 5.49 | 7.62
| 90 | 3.5 | 101.6 | 2.11 | 3.05 | 5.74 | 8.08
| 100 | 4 | 114.3 | 2.11 | 3.05 | 6.02 | 8.56
| 125 | 5 | 141.3 | 2.77 | 3.4 | 6.55 | 9.53
| 150 | 6 | 168.3 | 2.77 | 3.4 | 7.11 | 10.97
| 200 | 8 | 219.1 | 2.77 | 3.76 | 8.18 | 12.7
| 250 | 10 | 273.1 | 3.4 | 4.19 | 9.27 | 12.7
| 300 | 12 | 323.9 | 3.96 | 4.57 | 9.53 | 12.7
| 350 | 14 | 355.6 | 3.96 | 4.78 | 0 | 0
| 400 | 16 | 406.4 | 4.19 | 4.78 | 0 | 0
| 450 | 18 | 457 | 4.19 | 4.78 | 0 | 0
| 500 | 20 | 508 | 4.78 | 5.54 | 0 | 0
| 550 | 22 | 559 | 4.78 | 5.54 | 0 | 0
| 600 | 24 | 610 | 5.54 | 6.35 | 0 | 0
| 750 | 30 | 762 | 6.35 | 7.92 | 0 | 0
(Without input validation)
| HDPE PE100 Thickness (mm) and (in) ISO 4427 | [11 empty] | SI
| dn = Dext | dn (*) | Nominal pressures PN [bar] | [9 empty] | dn = | 160 | mm
| mm | in | 4 | 6 | 8 | 10 | 12.5 | 16 | 20 |  |  |  | PN = | 20 | bar
| 16 | 0.375 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 16 | 0
| 20 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 20 | 1 |  | Dext = | 160 | mm
| 25 | 0.75 | 0 | 0 | 0 | 0 | 0 | 2.3 | 2.8 | 25 | 2 |  | s = | 17.9 | mm
| 32 | 1 | 0 | 0 | 0 | 0 | 2.4 | 3 | 3.6 | 32 | 3 |  | Din = | 124.2 | mm
| 40 | 1.25 | 0 | 0 | 0 | 2.4 | 3 | 3.7 | 4.5 | 40 | 4
| 50 | 1.5 | 0 | 0 | 2.4 | 3 | 3.7 | 4.6 | 5.6 | 50 | 5
| 63 | 2 | 0 | 2.3 | 3 | 3.8 | 4.7 | 5.8 | 7.1 | 63 | 6
| 75 | 2.5 | 0 | 2.8 | 3.6 | 4.5 | 5.6 | 6.8 | 8.4 | 75 | 7 |  | Imperial
| 90 | 3 | 2.3 | 3.3 | 4.3 | 5.4 | 6.7 | 8.2 | 10.1 | 90 | 8
| 110 | 4 | 2.7 | 4 | 5.3 | 6.6 | 8.1 | 10 | 12.3 | 110 | 9 |  | dn = | 6 | in
| 125 | 5 | 3.1 | 4.6 | 6 | 7.4 | 9.2 | 11.4 | 14 | 125 | 10 |  | PN = | 20 | bar
| 140 | 5.5 | 3.5 | 5.1 | 6.7 | 8.3 | 10.3 | 12.7 | 15.7 | 140 | 11
| 160 | 6 | 4 | 5.8 | 7.7 | 9.5 | 11.8 | 14.6 | 17.9 | 160 | 12 |  | Dext = | 160 | mm
| 180 | 7 | 4.4 | 6.6 | 8.6 | 10.7 | 13.3 | 16.4 | 20.1 | 180 | 13 |  | s = | 17.9 | mm
| 200 | 8 | 4.9 | 7.3 | 9.6 | 11.9 | 14.7 | 18.2 | 22.4 | 200 | 14 |  | Din = | 124.2 | mm
| 225 | 9 | 5.5 | 8.2 | 10.8 | 13.4 | 16.6 | 20.5 | 25.2 | 225 | 15
| 250 | 10 | 6.2 | 9.1 | 11.9 | 14.8 | 18.4 | 22.7 | 27.9 | 250 | 16
| 280 | 11 | 6.9 | 10.2 | 13.4 | 16.6 | 20.6 | 25.4 | 31.3 | 280 | 17 |  | Note (*)
| 315 | 12 | 7.7 | 11.4 | 15 | 18.7 | 23.2 | 28.6 | 35.2 | 315 | 18 |  | Nominal diameters in inches in
| 355 | 14 | 8.7 | 12.9 | 16.9 | 21.1 | 26.1 | 32.2 | 39.7 | 355 | 19 |  | red colour are not defined in the
| 400 | 16 | 9.8 | 14.5 | 19.1 | 23.7 | 29.4 | 36.3 | 44.7 | 400 | 20 |  | imperial denomination
| 450 | 18 | 11 | 16.3 | 21.5 | 26.7 | 33.1 | 40.9 | 50.3 | 450 | 21
| 500 | 20 | 12.3 | 18.1 | 23.9 | 29.7 | 36.8 | 45.4 | 55.8 | 500 | 22
| 560 | 22 | 13.7 | 20.3 | 26.7 | 33.2 | 41.2 | 50.8 | 0 | 560 | 23
| 630 | 24 | 15.4 | 22.8 | 30 | 37.4 | 46.2 | 57.2 | 0 | 630 | 24
| 710 | 28 | 17.4 | 25.7 | 33.9 | 42.1 | 52.2 | 0 | 0 | 710 | 25
| 800 | 32 | 19.6 | 29 | 38.1 | 47.4 | 58.8 | 0 | 0 | 800 | 26
| 900 | 36 | 22 | 32.6 | 42.6 | 53.3 | 0 | 0 | 0 | 900 | 27
| 1000 | 40 | 24.5 | 36.2 | 47.7 | 59.3 | 0 | 0 | 0 | 1000 | 28
| 1200 | 48 | 29.4 | 43.4 | 57.2 |  | 0 | 0 | 0 | 1200 | 29
| 1400 | 54 | 34.3 | 50.6 | 0 |  | 0 | 0 | 0 | 1400 | 30
| 1600 | 64 | 39.2 | 57.9 | 0 |  | 0 | 0 | 0 | 1600 | 31
|  |  | 4 | 6 | 8 | 10 | 12.5 | 16 | 20
http://www.soheval.cl/files/Tablas_tecnicas.pdf
ISO 4427 PE 100 Design stress 8.0 MPa
For info., http://www.krah.cl/wp-content/uploads/2013/10/catalogo_krah_final_baja.pdf
Thickness of HDPE PE80 pipe DIN 8074 / ISO 4427
(Without input validation)
| dn = Dext | dn (*) | Nominal pressure PN [bar]
| mm | in | 2.5 | 3.2 | 4 | 6 | 10 | 16 |  | SI |  |  | Imperial
0.1 | 16 | 0.375 | 0 | 0 | 0 | 0 | 0 | 2.2
1 | 20 | 0.5 | 0 | 0 | 0 | 0 | 1.9 | 2.8 |  | dn = | 40 | mm | dn = | 1.25 | in
1.9 | 25 | 0.75 | 0 | 0 | 0 | 0 | 2.3 | 3.5 |  | PN = | 10 | bar | PN = | 10 | bar
2.8 | 32 | 1 | 0 | 0 | 0 | 1.8 | 2.9 | 4.4
3.7 | 40 | 1.25 | 0 | 0 | 1.8 | 2.3 | 3.7 | 5.5 |  | Dext = | 40 | mm | Dext = | 40 | mm
4.6 | 50 | 1.5 | 0 | 1.8 | 2 | 2.9 | 4.6 | 6.9 |  | s = | 3.7 | mm | s = | 3.7 | mm
5.5 | 63 | 2 | 1.8 | 2 | 2.5 | 3.6 | 5.8 | 8.6 |  | Din = | 32.6 | mm | Din = | 32.6 | mm
6.4 | 75 | 2.5 | 1.9 | 2.3 | 2.9 | 4.3 | 6.8 | 10.3
7.3 | 90 | 3 | 2.2 | 2.8 | 3.5 | 5.1 | 8.2 | 12.3 | [5 empty] | 32.6
8.2 | 110 | 4 | 2.7 | 3.4 | 4.2 | 6.3 | 10 | 15.1
9.1 | 125 | 5 | 3.1 | 3.9 | 4.8 | 7.1 | 11.4 | 17.1
10 | 140 | 5.5 | 3.5 | 4.3 | 5.4 | 8 | 12.7 | 19.2
10.9 | 160 | 6 | 4 | 4.9 | 6.2 | 9.1 | 14.6 | 21.9
11.8 | 180 | 7 | 4.4 | 5.5 | 6.9 | 10.2 | 16.4 | 24.6
12.7 | 200 | 8 | 4.9 | 6.2 | 7.7 | 11.4 | 18.2 | 27.4 |  | Note (*)
13.6 | 225 | 9 | 5.5 | 6.9 | 8.6 | 12.8 | 20.5 | 30.8 |  | Nominal diameters in inches in
14.5 | 250 | 10 | 6.2 | 7.7 | 9.6 | 14.2 | 22.7 | 34.2 |  | red colour are not defined in the
15.4 | 280 | 11 | 6.9 | 8.6 | 10.7 | 15.9 | 25.4 | 38.3 |  | imperial denomination
16.3 | 315 | 12 | 7.7 | 9.7 | 12.1 | 17.9 | 28.6 | 43.1
17.2 | 355 | 14 | 8.7 | 10.9 | 13.6 | 20.1 | 32.2 | 48.5
18.1 | 400 | 16 | 9.8 | 12.3 | 15.3 | 22.7 | 36.3 | 54.7
19 | 450 | 18 | 11 | 13.8 | 17.2 | 25.5 | 40.9 | 61.5
19.9 | 500 | 20 | 12.3 | 15.3 | 19.1 | 28.4 | 45.4 | 68.3
20.8 | 560 | 22 | 13.7 | 17.2 | 21.4 | 31.7 | 50.8 | 0
21.7 | 630 | 24 | 15.4 | 19.3 | 24.1 | 35.7 | 57.2 | 0
22.6 | 710 | 28 | 17.4 | 21.8 | 27.2 | 40.2 | 64.5 | 0
23.5 | 800 | 32 | 19.6 | 24.5 | 30.6 | 45.3 | 0 | 0
24.4 | 900 | 36 | 22 | 27.6 | 34.4 | 51 | 0 | 0
25.3 | 1000 | 40 | 24.5 | 30.6 | 38.2 | 56.7 | 0 | 0
26.2 | 1100 | 44 | 26.9 | 33.7 | 42 | 62.4 | 0 | 0
27.1 | 1200 | 48 | 29.4 | 36.7 | 45.9 | 68 | 0 | 0
28 | 1400 | 54 | 34.4 | 42.9 | 53.5 | 0 | 0 | 0
28.9 | 1600 | 64 | 39.2 | 49 | 61.2 | 0 | 0 | 0
|  |  | 2.5 | 3.2 | 4 | 6 | 10 | 16
ISO 4427 PE 80 Design stress 6.3 MPa