## A.- Fund. Hum. Param. (hidden)
Fundamental humidity parameters
5.- Humidity ratio "x" | 7.- Specific humidity "q" | 9a.- Density of moist air
The humidity ratio, also moisture content | The specific humidity is the ratio of the | The density of a moist air mixture is
or Absolute humidity, is the ratio of the | mass of water vapor to the total mass. | the ratio of the total mass to the total
mass of water "Mw" to the mass of dry |  | volume.
air "Ma".
and in terms of the absolute humidiry
6.- Mole fractiion "nfi"
Mole fraction of a given component "i"
is equal to the number of moles "ni"
divided by the total number of
components "n" in the mixture.
The mol fraction of dry air is "nfa" and
the mol fraction of water vapor is "nfw"
9.- Water vapor density "rv"
Water vapor density is the ratio of the
mass of water to the total volume.

## B.- Hum. Param. Involv. Sat. (hidden)
10.- Saturation humidity ratio. | [9 empty] | 14. -Thermodynamic wet-bulb temperature
Saturation humidity ratio Ws(t,p) is the | [9 empty] | temperature "twb" (or t*)
humidity ratio of moist air saturated
with respect to water at the same
teemperature "t" and pressure "p"
11.- Degree of saturation "m"
The degree of saturation is the ratio of
the absolute humidity "x" to the absolute
humidity of the saturated air "xs" at the
same temperature and pressure
12.- Relative humidity
The relative humidity "f" is the ratio of
the mol fraction of water vapor "nfw" in
a given moist air sample, to the mol
fraction "nfws" in an air sample, saturated
at the same temperature and pressure.
13.- Dew point temperature
The dew point temperature "tdp" is the
temperature of moist air, saturated at
the same pressure "p", with the same
absolute humidity as that of the given
sample of moisat air.
It is defined as the solution tdp(p,x) of
the equation
| From graphic |  |  | Using function Sicro_Dew_point |  |  | Using function DewPoint
| tdb = | 37.8 | °C | tdb = | 37.7778 | ºC | p = | 14.696 | psia
| f = | 31.4 | % | twb = | 23.8889 | ºC | x = | 0.0133 | lb/lb
| x = | 0.0133 | g/kg | H = | 3.3528 | m | tdp = | #NAME? | °F
| tdp = | 17.8 | °C | tdp = | 17.836 | ºC |  | #NAME? | °C
37.8
23.9
37.8
0.01876
0.01292
17.8
31.4%

## Air Data (hidden)
-73.15 | 0.0181 | 1.007 | 0.737 | 1.7458 | 1.325e-05
-23.15 | 0.0223 | 1.006 | 0.72 | 1.3947 | 1.596e-05 | Application example
26.85 | 0.0263 | 1.007 | 0.707 | 1.1614 | 1.846e-05
76.85 | 0.03 | 1.009 | 0.7 | 0.995 | 2.082e-05 | Input data: Temperature | t = | 35 | ºC
126.85 | 0.0338 | 1.014 | 0.69 | 0.8711 | 2.301e-05
176.85 | 0.0373 | 1.021 | 0.686 | 0.774 | 2.507e-05 | Function used |  | Results
226.85 | 0.0407 | 1.03 | 0.684 | 0.6964 | 2.701e-05 | AirConductivity_t(t) | k = | 0.0269 | W/(m*K)
276.85 | 0.0439 | 1.04 | 0.683 | 0.6329 | 2.884e-05 | AirSpecificHeat_t(t) | Cp = | 1.0073 | kJ/kg
326.85 | 0.0469 | 1.051 | 0.685 | 0.5804 | 3.058e-05 | AirPrandtl_t(t) | Pr = | 0.706 | -
376.85 | 0.0497 | 1.063 | 0.69 | 0.5356 | 3.225e-05 | AirDensity_t(t) | r = | 1.1343 | kg/m3
426.85 | 0.0524 | 1.075 | 0.695 | 0.4975 | 3.388e-05 | AirAbsoluteViscosity | m = | 1.8845e-05 | Pa*s
476.85 | 0.0549 | 1.087 | 0.702 | 0.4643 | 3.546e-05 | AirKinematicViscosity_t(t) | n = | 1.6614e-05 | m2/s
526.85 | 0.0573 | 1.099 | 0.709 | 0.4354 | 3.698e-05 | AirThermalDiffusivity_t(t) | a = | 2.3544e-05 | m2/s
576.85 | 0.0596 | 1.11 | 0.716 | 0.4097 | 3.843e-05
626.85 | 0.062 | 1.121 | 0.72 | 0.3868 | 3.981e-05
676.85 | 0.0643 | 1.131 | 0.723 | 0.3666 | 4.113e-05
726.85 | 0.0667 | 1.141 | 0.726 | 0.3482 | 4.244e-05
t | k | Cp | Pr | ragua | m
ºC | W/(m*K) | kJ/(kg*K) | - | kg/m3 | Pa s
Atmospheric air properties as a function of the temperature

## Water Data (hidden)
0 | 0.569 | 4.217 | 12.99 | 1000 | 0.00175 | 1.75e-06 | 1.3493e-07 | 0.006108
1.85 | 0.574 | 4.211 | 12.22 | 1000 | 0.001652 | 1.652e-06 | 1.3631e-07 | 0.0069793 |  | Application example
6.85 | 0.582 | 4.198 | 10.26 | 1000 | 0.001422 | 1.422e-06 | 1.3864e-07 | 0.0099092
11.85 | 0.59 | 4.189 | 8.81 | 1000 | 0.001225 | 1.225e-06 | 1.4085e-07 | 0.013876 |  | Input data: Temperature | t = | 35 | ºC
16.85 | 0.598 | 4.184 | 7.56 | 999.001 | 0.00108 | 1.0811e-06 | 1.4307e-07 | 0.019178
21.85 | 0.606 | 4.181 | 6.62 | 998.004 | 0.000959 | 9.6092e-07 | 1.4523e-07 | 0.026181 |  | Function used |  | Results
26.85 | 0.613 | 4.179 | 5.83 | 997.009 | 0.000855 | 8.5756e-07 | 1.4713e-07 | 0.035323 |  | SaturatedWaterConductivity_t | k = | 0.625 | W/(m*K)
31.85 | 0.62 | 4.178 | 5.2 | 995.0249 | 0.000769 | 7.7284e-07 | 1.4914e-07 | 0.047132 |  | SaturatedWaterSpecificHeat_t | Cp = | 4.178 | kJ/kg
36.85 | 0.628 | 4.178 | 4.62 | 993.0487 | 0.000695 | 6.9986e-07 | 1.5136e-07 | 0.062228 |  | SaturatedWaterPrandtl_t | Pr = | 4.835 | -
41.85 | 0.634 | 4.179 | 4.16 | 991.0803 | 0.000631 | 6.3668e-07 | 1.5308e-07 | 0.081341 |  | SaturatedWaterDensity_t | r = | 993.7798 | kg/m3
46.85 | 0.64 | 4.18 | 3.77 | 989.1197 | 0.000577 | 5.7758e-07 | 1.5326e-07 | 0.10532 |  | SaturatedWaterAbsoluteViscosity_t | m = | 0.00072238 | Pa*s
51.85 | 0.645 | 4.182 | 3.42 | 987.1668 | 0.000528 | 5.3486e-07 | 1.5624e-07 | 0.13513 |  | SaturatedWaterKinematicViscosity_t | n = | 7.269e-07 | m2/s
56.85 | 0.651 | 4.184 | 3.15 | 984.252 | 0.000489 | 4.9682e-07 | 1.5784e-07 | 0.1719 |  | SaturatedWaterThermalDiffusivity_t | a = | 1.505e-07 | m2/s
61.85 | 0.656 | 4.186 | 2.88 | 982.3183 | 0.000453 | 4.6115e-07 | 1.5953e-07 | 0.21689
66.85 | 0.66 | 4.188 | 2.66 | 979.4319 | 0.00042 | 4.2882e-07 | 1.609e-07 | 0.27153
71.85 | 0.664 | 4.191 | 2.45 | 976.5625 | 0.000389 | 3.9834e-07 | 1.6321e-07 | 0.33742
76.85 | 0.668 | 4.195 | 2.29 | 973.7098 | 0.000365 | 3.7485e-07 | 1.6354e-07 | 0.41632
81.85 | 0.671 | 4.199 | 2.14 | 970.8738 | 0.000343 | 3.5329e-07 | 1.6459e-07 | 0.51022
86.85 | 0.674 | 4.203 | 2.02 | 967.118 | 0.000324 | 3.3502e-07 | 1.6581e-07 | 0.62127
91.85 | 0.677 | 4.209 | 1.91 | 963.3911 | 0.000306 | 3.1763e-07 | 1.6696e-07 | 0.75183
96.85 | 0.679 | 4.214 | 1.8 | 960.6148 | 0.000289 | 3.0085e-07 | 1.6774e-07 | 0.90449
100 | 0.68 | 4.217 | 1.76 | 957.8544 | 0.000279 | 2.9128e-07 | 1.6835e-07 | 1.0133
t | k | Cp | Pr | ragua | m | n | a | Psat
ºC | W/(m*K) | kJ/(kg*K) | - | kg/m3 | Pa s | m2/s | m2/s | bar | K
Saturation properties of water as a function of the temperature

## H = 0 m.a.s.l.
Rev. cjc.17.05.2016
H = | 0 | m.a.s.l.
Sicro_Absolute_Humidity_tdb_f_H
tdb | Relative humidity f = Sicro_Absolute_Humidity_tdb_f_H [%]
ºC | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
0 | 0.00037542 | 0.00075129 | 0.0011276 | 0.0015044 | 0.0018816 | 0.0022593 | 0.0026375 | 0.0030161 | 0.0033952 | 0.0037747
5 | 0.00053604 | 0.001073 | 0.0016109 | 0.0021497 | 0.0026895 | 0.0032301 | 0.0037718 | 0.0043143 | 0.0048578 | 0.0054023
10 | 0.00075472 | 0.0015113 | 0.0022697 | 0.0030299 | 0.003792 | 0.004556 | 0.0053218 | 0.0060895 | 0.006859 | 0.0076305
15 | 0.0010487 | 0.0021008 | 0.0031566 | 0.0042159 | 0.0052789 | 0.0063454 | 0.0074156 | 0.0084894 | 0.0095669 | 0.010648
20 | 0.001439 | 0.0028847 | 0.0043371 | 0.0057962 | 0.0072622 | 0.008735 | 0.010215 | 0.011701 | 0.013195 | 0.014696
25 | 0.0019515 | 0.0039153 | 0.0058915 | 0.0078803 | 0.0098816 | 0.011896 | 0.013923 | 0.015963 | 0.018016 | 0.020082
30 | 0.0026174 | 0.0052569 | 0.0079188 | 0.010603 | 0.013311 | 0.016042 | 0.018796 | 0.021575 | 0.024377 | 0.027204
35 | 0.0034739 | 0.0069869 | 0.01054 | 0.014133 | 0.017767 | 0.021442 | 0.025161 | 0.028922 | 0.032728 | 0.036578
40 | 0.0045656 | 0.0091987 | 0.013901 | 0.018674 | 0.023519 | 0.028437 | 0.033432 | 0.038503 | 0.043654 | 0.048886
45 | 0.0059451 | 0.012005 | 0.018183 | 0.024482 | 0.030907 | 0.037461 | 0.044147 | 0.050971 | 0.057936 | 0.065046
50 | 0.0076745 | 0.015541 | 0.023606 | 0.031878 | 0.040365 | 0.049075 | 0.058017 | 0.0672 | 0.076635 | 0.086332
55 | 0.0098269 | 0.019969 | 0.030443 | 0.041264 | 0.052449 | 0.064019
60 | 0.012488 | 0.025488 | 0.039032 | 0.053155
65 | 0.015759 | 0.032338 | 0.049802
70 | 0.019759 | 0.040815 | 0.063299
75 | 0.024628 | 0.051287
80 | 0.030532
85 | 0.037671
90 | 0.046286
95 | 0.056668
100
tdb | Enthalpy h = Sicro_Absolute_Humidity_tdb_ent [kJ/kg]
ºC | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120
0 | 0 | 0.0039984 | 0.0079968 | 0.011995
5 |  | 0.001992 | 0.005976 | 0.0099601 | 0.013944
10 |  | 0 | 0.0039698 | 0.0079395 | 0.011909 | 0.015879 | 0.019849 | 0.023819 | 0.027788 | 0.031758 | 0.035728 | 0.039698 | 0.043667
15 |  |  | 0.0019778 | 0.0059334 | 0.0098889 | 0.013845 | 0.0178 | 0.021756 | 0.025711 | 0.029667 | 0.033622 | 0.037578 | 0.041534
20 |  |  | 0 | 0.0039415 | 0.007883 | 0.011825 | 0.015766 | 0.019708 | 0.023649 | 0.027591 | 0.031532 | 0.035474 | 0.039415
25 |  |  |  | 0.0019638 | 0.0058913 | 0.0098188 | 0.013746 | 0.017674 | 0.021601 | 0.025529 | 0.029457 | 0.033384 | 0.037312
30 |  |  |  | 0 | 0.0039137 | 0.0078273 | 0.011741 | 0.015655 | 0.019568 | 0.023482 | 0.027396 | 0.031309 | 0.035223
35 |  |  |  |  | 0.0019499 | 0.0058498 | 0.0097497 | 0.01365 | 0.01755 | 0.021449 | 0.025349 | 0.029249 | 0.033149
40 |  |  |  |  | 0 | 0.0038862 | 0.0077724 | 0.011659 | 0.015545 | 0.019431 | 0.023317 | 0.027203 | 0.03109
45 | [5 empty] | 0.0019363 | 0.0058089 | 0.0096816 | 0.013554 | 0.017427 | 0.021299 | 0.025172 | 0.029045
50 | [5 empty] | 0 | 0.0038591 | 0.0077183 | 0.011577 | 0.015437 | 0.019296 | 0.023155 | 0.027014
55
60
65
70
75
80
85
90
95
100
tdb | Wet bulb temperature twb = Sicro_Absolute_Humidity_tdb_twb_H [ºC]
ºC | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40
0 | 0.0037747
5 | 0.0017691 | 0.0054023
10 | -0.0002221 | 0.0033812 | 0.0076305
15 | -0.0021991 | 0.0013748 | 0.0055917 | 0.010648
20 |  | -0.0006173 | 0.0035677 | 0.0085885 | 0.014696
25 |  | -0.0025951 | 0.0015582 | 0.0065439 | 0.012612 | 0.020082
30 |  | -0.0045589 | -0.00043678 | 0.004514 | 0.010542 | 0.017968 | 0.027204
35 |  |  | -0.0024175 | 0.0024989 | 0.0084883 | 0.015869 | 0.025053 | 0.036578
40 |  |  | -0.0043841 | 0.00049817 | 0.006449 | 0.013786 | 0.022918 | 0.034382 | 0.048886
45 |  |  | -0.0063368 | -0.0014882 | 0.0044245 | 0.011717 | 0.020799 | 0.032201 | 0.046632
50 |  |  |  | -0.0034604 | 0.0024146 | 0.009664 | 0.018695 | 0.030037 | 0.044396
55 |  |  |  | -0.0054185 | 0.00041912 | 0.0076256 | 0.016606 | 0.027889 | 0.042176
60 |  |  |  | -0.0073628 | -0.0015621 | 0.0056018 | 0.014532 | 0.025757 | 0.039972
65 |  |  |  | -0.0092933 | -0.0035293 | 0.0035926 | 0.012474 | 0.02364 | 0.037785
70 |  |  |  |  | -0.0054824 | 0.0015977 | 0.01043 | 0.021538 | 0.035614
75 |  |  |  |  | -0.0074218 | -0.00038292 | 0.0084016 | 0.019452 | 0.033459
80 |  |  |  |  | -0.0093475 | -0.0023495 | 0.0063872 | 0.017381 | 0.031319
85 |  |  |  |  | -0.01126 | -0.0043021 | 0.0043872 | 0.015325 | 0.029195
90 |  |  |  |  | -0.013158 | -0.006241 | 0.0024015 | 0.013283 | 0.027086
95 | [5 empty] | -0.0081662 | 0.00042977 | 0.011256 | 0.024992
100 | [5 empty] | -0.010078 | -0.001528 | 0.0092439 | 0.022914
f =100 %
f =90 %
f =80 %
f =70 %
f =60 %
f =50 %
f = 40 %
f =30 %
f =20 %
f =10 %
h = 100 kJ/kg
h = 90 kJ/kg
h = 80 kJ/kg
h = 70 kJ/kg
h = 60 kJ/kg
h = 50 kJ/kg
h = 40 kJ/kg
h = 10 kJ/kg
h = 20 kJ/kg
h = 30 kJ/kg
twb = 20 ºC
twb = 30 ºC
twb = 35 ºC
twb = 40 ºC
twb = 10 ºC
twb = 25 ºC
twb = 15 ºC
twb = 10 ºC
twb = 5 ºC
x kg/kg
h = 110 kJ/kg
h = 120 kJ/kg

## H = 5300 m.a.s.l.
Rev. cjc.17.05.2016
H = | 5300 | m.a.s.l. |  |  | Sicro_Absolute_Humidity_tdb_f_H
tdb | Relative humidity f = Sicro_Absolute_Humidity_tdb_f_H [%]
ºC | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
0 | 0.00073351 | 0.0014688 | 0.0022057 | 0.0029445 | 0.0036849 | 0.0044272 | 0.0051712 | 0.0059169 | 0.0066645 | 0.0074138
5 | 0.0010476 | 0.0020987 | 0.0031534 | 0.0042116 | 0.0052735 | 0.0063389 | 0.007408 | 0.0084807 | 0.0095571 | 0.010637
10 | 0.0014755 | 0.0029579 | 0.0044475 | 0.0059441 | 0.007448 | 0.008959 | 0.010477 | 0.012003 | 0.013536 | 0.015076
15 | 0.002051 | 0.0041156 | 0.0061939 | 0.0082861 | 0.010392 | 0.012512 | 0.014647 | 0.016796 | 0.018959 | 0.021138
20 | 0.0028162 | 0.0056579 | 0.0085257 | 0.01142 | 0.014341 | 0.017288 | 0.020264 | 0.023267 | 0.026298 | 0.029358
25 | 0.0038222 | 0.0076917 | 0.011609 | 0.015576 | 0.019593 | 0.02366 | 0.02778 | 0.031952 | 0.036179 | 0.04046
30 | 0.0051316 | 0.010349 | 0.015653 | 0.021047 | 0.026534 | 0.032114 | 0.037792 | 0.043569 | 0.049448 | 0.055432
35 | 0.0068199 | 0.013791 | 0.020918 | 0.028208 | 0.035664 | 0.043293 | 0.051101 | 0.059095 | 0.067281
40 | 0.0089781 | 0.018219 | 0.027735 | 0.037538 | 0.047641 | 0.058059
45 | 0.011716 | 0.023881 | 0.036523 | 0.04967 | 0.063352
50 | 0.015164 | 0.031087 | 0.047825 | 0.065444
55 |  |  | 0.062354
60
65
70
75
80
85
90
95
100
tdb | Enthalpy h = Sicro_Absolute_Humidity_tdb_ent [kJ/kg]
ºC | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
0 | 0 | 0.0039984 | 0.0079968 | 0.011995
5 |  | 0.001992 | 0.005976 | 0.0099601 | 0.013944
10 |  | 0 | 0.0039698 | 0.0079395 | 0.011909 | 0.015879 | 0.019849 | 0.023819 | 0.027788 | 0.031758 | 0.035728
15 |  |  | 0.0019778 | 0.0059334 | 0.0098889 | 0.013845 | 0.0178 | 0.021756 | 0.025711 | 0.029667 | 0.033622
20 |  |  | 0 | 0.0039415 | 0.007883 | 0.011825 | 0.015766 | 0.019708 | 0.023649 | 0.027591 | 0.031532
25 |  |  |  | 0.0019638 | 0.0058913 | 0.0098188 | 0.013746 | 0.017674 | 0.021601 | 0.025529 | 0.029457
30 |  |  |  | 0 | 0.0039137 | 0.0078273 | 0.011741 | 0.015655 | 0.019568 | 0.023482 | 0.027396
35 |  |  |  |  | 0.0019499 | 0.0058498 | 0.0097497 | 0.01365 | 0.01755 | 0.021449 | 0.025349
40 |  |  |  |  | 0 | 0.0038862 | 0.0077724 | 0.011659 | 0.015545 | 0.019431 | 0.023317
45 | [5 empty] | 0.0019363 | 0.0058089 | 0.0096816 | 0.013554 | 0.017427 | 0.021299
50 | [5 empty] | 0 | 0.0038591 | 0.0077183 | 0.011577 | 0.015437 | 0.019296
55
60
65
70
75
80
85
90
95
100
tdb | Wet bulb temperature twb = Sicro_Absolute_Humidity_tdb_twb_H [ºC]
ºC | 0 | 5 | 10 | 15 | 20 | 25 | 30
0 | 0.0074138
5 | 0.0053951 | 0.010637
10 | 0.0033909 | 0.0085972 | 0.015076
15 | 0.001401 | 0.006572 | 0.013011 | 0.021138
20 |  | 0.0045613 | 0.01096 | 0.01904 | 0.029358
25 |  | 0.0025649 | 0.0089237 | 0.016957 | 0.02722 | 0.04046
30 |  | 0.00058278 | 0.0069022 | 0.01489 | 0.025097 | 0.03827 | 0.055432
35 |  |  | 0.0048952 | 0.012837 | 0.02299 | 0.036097 | 0.053177
40 |  |  | 0.0029026 | 0.010799 | 0.020898 | 0.03394 | 0.050938
45 |  |  | 0.00092402 | 0.0087758 | 0.018822 | 0.031798 | 0.048715
50 |  |  |  | 0.006767 | 0.01676 | 0.029672 | 0.046509
55 |  |  |  | 0.0047725 | 0.014713 | 0.027561 | 0.044319
60 |  |  |  | 0.0027921 | 0.012681 | 0.025465 | 0.042145
65 |  |  |  | 0.00082569 | 0.010663 | 0.023385 | 0.039987
70 |  |  |  |  | 0.0086594 | 0.021319 | 0.037844
75 |  |  |  |  | 0.00667 | 0.019268 | 0.035716
80 |  |  |  |  | 0.0046947 | 0.017232 | 0.033604
85 |  |  |  |  | 0.0027332 | 0.01521 | 0.031507
90 |  |  |  |  | 0.00078545 | 0.013202 | 0.029425
95 | [5 empty] | 0.011209 | 0.027357
100 | [5 empty] | 0.009229 | 0.025305
x kg/kg
twb = 0 ºC
twb = 5 ºC
twb = 10 ºC
twb = 15 ºC
twb = 20 ºC
twb = 25 ºC
twb = 30 ºC
f =100 %
f =90 %
f =80 %
f =70 %
f =60 %
f =50 %
f = 40 %
f =30 %
f =20 %
f =10 %
h = 100 kJ/kg
h = 90 kJ/kg
h = 80 kJ/kg
h = 70 kJ/kg
h = 60 kJ/kg
h = 50 kJ/kg
h = 40 kJ/kg
h = 10 kJ/kg
h = 20 kJ/kg
h = 30 kJ/kg

## Table
Rev. cjc.17.05.2016
Psychrometric Functions
| Dry bulb temperature |  | tdb | °C |  | Absolute humidity |  | x | kg w/kg da |  | Dew point temperature |  | tdp | ºC
| Relative humidity |  | f | % |  | Specific volume |  | v | m3/kg da |  | Specific enthalpy |  | ent | kJ/kg da
| Height above sea level |  | H | m.a.s.l. |  | Density |  | r | kg /m3 |  | Wet bulb temperature |  | twb | ºC
| Maximum values for the input parameters |  |  |  | - At altitudes above sea level with, "H < Hmax", the routine can handle relative humidities "f" greater than the given value "fMax". The maximum values of
| tdbMax = | 96 | °C |  | the dry bulb temperature, relative humidity and height above sea level, are defined in order to obtain an acceptable maximum number of iterations. These
| f Max = | 60 | % |  | range limitations are required only in the functions calculating the wet bulb temperature (functions 16, 36, 46 and 56).
| Hmax = | 5300 | m.a.s.l. |  | - The numbers in square brakets indicate the number of the function in the VBA environment
Groups
|  |  | Group 1 |  |  | Group 2 |  |  | Group 3 |  |  | Group 4 |  |  | Group 5
|  |  | tdb, f , H |  |  | tdb, twb, H |  |  | tdb, x, H |  |  | ent, x, H |  |  | tdb, ent, H
tdb | ºC | tdb | 21 | °C | tdb | 21 | °C | tdb | 21 | °C | tdb | 21 | [48] | tdb | 21 | °C
f | % | f | 31.45 | % | f | 31.4518 | [27] | f | 31.45 | [37] | f | 31.45 | [47] | f | 31.45 | [57]
H | m s.n.m. | H | 10 | m | H | 10 | m | H | 10 | m | H | 10 | m | H | 10 | m
x | kg/kg | x | 0.0048457 | [11] | x | 0.004846 | [21] | x | 0.0048457 | kg/kg | x | 0.0048457 | kg/kg | x | 0.0048457 | [51]
v | m3/kg | v | 0.84082 | [12] | v | 0.84083 | [22] | v | 0.84082 | [32] | v | 0.84082 | [42] | v | 0.84082 | [52]
r | kg/m3 | r | 1.1951 | [13] | r | 1.1951 | [23] | r | 1.1951 | [33] | r | 1.1951 | [43] | r | 1.1951 | [53]
tdp | ºC | tdp | 3.4377 | [14] | tdp | 3.4385 | [24] | tdp | 3.4377 | [34] | tdp | 3.4377 | [44] | tdp | 3.4377 | [54]
ent | kJ/kg | ent | 33.3029 | [15] | ent | 33.3036 | [25] | ent | 33.3029 | [35] | ent | 33.3029 | kJ/kg | ent | 33.3029 | KJ/kg
twb | ºC | twb | 11.7734 | [16] | twb | 11.7734 | ºC | twb | 11.7734 | [36] | twb | 11.7734 | [46] | twb | 11.7734 | [56]

## Process
Nat-Nat diagram
|  |  |  | x = | x1 + (t - t1 ) * (x2 - x1) / (t2 - t1)
Specification for point 1
Temperature | t1 = | 37 | ºC | t1 = | 37 | ºC
Relative humidity | f1 = | 50 | % | t2 = | 25 | ºC
| H = | 0 | m.a.s.l. | x1 = | 0.019895 | kg/kg
|  |  |  | x2 = | 0.0098816 | kg/kg
| x1 = | 0.019895 | kg/kg
|  |  |  | t | x
Specification for point 2 |  |  |  | ºC | kg/kg
Temperature | t2 = | 25 | ºC | 25 | 0.0098816
Relative humidity | f2 = | 50 | % | 26 | 0.010716
| H = | 0 | m.a.s.l. | 27 | 0.01155
|  |  |  | 28 | 0.012385
| x2 = | 0.0098816 | kg/kg | 29 | 0.013219
|  |  |  | 30 | 0.014054
|  |  |  | 31 | 0.014888
|  |  |  | 32 | 0.015722
|  |  |  | 33 | 0.016557
|  |  |  | 34 | 0.017391
|  |  |  | 35 | 0.018226
|  |  |  | 36 | 0.01906
In the psychrometric chart for height above sea level H = 0 m.a.s.l |  |  |  | 37 | 0.019895
I have included the proces 1 - 2 wich consist of a linear function
x = function (t)
The equation for this function is shown in sheet Process.
For adding the information of a process line in a psychrometric chart, see sheet "H = 0 m.a.s.l"
x
t
t1
x1
t2
t
x
x2
②
①
PPP
P
t2 - t1
x - x1
t - t1
x2 - x1

## Ref_1
Other references related to psychrometry, see
www.piping-tools.net