## Index of functions
Steamdat functions (Note 1) | [10 empty] | Rev. cjc 01.06.2016
Saturation properties |  |  |  | Humid region |  |  |  | Superheated steam
p = |  | 140 | bar | p = |  | 140 | bar | p = |  | 140 | bar
|  |  |  | x = |  | 0.8 |  | t = |  | 500 | ºC
sf (p) = | SaturWater_Entropy_p | 3.623 | kJ(kg K) | t (p) = | H2O_SaturationTemp_p(I2) | 336.6414 | ºC | s (t,p) = | H2O_Entropy_t_p(t,p) | 6.3937 | kJ/(kg K)
t (p) = | H2O_SaturationTemp_p(p) | 336.6694 | ºC | h (p,x) = | H2O_Enthalpy_p_x(I2,I3) | 2428.22 | kJ/kg | h (t,p) = | H2O_Enthalpy_t_p(t,p) | 3323.8262 | kJ/kg
h (t) = | SaturWater_Enthalpy_t(t) | 1570.8785 | kJ/kg | s (p,h) = | H2O_Entropy_p_h(I2,I5) | 5.029 | kJ/(kg K) | v (t,p) = | H2O_SpecVolume_p_h(t,p) | 0.022509 | m3/kg
Saturated water |  |  |  | h (p,x) = | H2O_Enthalpy_p_x(I2,I3) | 2428.22 | kJ/kg | m (t,p) = | H2O_DynViscosity_t_p(t,p) | 2.9179e-05 | Pa s
p (s) = | H2O_SaturationPressure_s(s) | 139.9999 | bar | h (t,x) = | H2O_Enthalpy_t_x(I4,I3) | 2428.22 | kJ/kg | h (p,s) = | H2O_Enthalpy_p_s(p,s) | 3323.8262 | kJ/kg
p (t) = | H2O_SaturationPressure_t(t) | 140 | bar | v (p,x) = | H2O_SpecVolume_p_x(p,x) | 0.0095182 |  | h (t,p) = | H2O_Enthalpy_t_p(t,p) | 3323.8262 | kJ/kg
|  |  |  | v (t,x) = | H2O_SpecVolume_t_x(t,x) | 0.0095182 |  | h (t,s) = | H2O_Enthalpy_t_s(t,s) | 3323.8262 | kJ/kg
t (s) = | H2O_SaturationTemp_s(s) | 336.6693 | ºC | hfg (p) = | H2O_VapourisationHeat_p(p) | 1070.7324 | kJ/kg | s (p,h) = | H2O_Entropy_p_h(p,h) | 6.3937 | kJ/(kg K)
m (t) = | SaturWater_DynViscosity_t(t) | 7.1837e-05 | Pa s | hfg (t) = | H2O_VapourisationHeat_t(t) | 1070.7324 | kJ/kg | s (t,p) = | H2O_Entropy_t_p(t,p) | 6.3937 | kJ/(kg K)
h (p) = | SaturWater_Enthalpy_p(p) | 1570.8785 | kJ/kg | x (p,h) = | SteamQuality_p_h(p,h) | 0.8 | - | k (t,p) = | H2O_HeatConductivity_t_p(t,p) | 0.080056 | W/(m K)
h (t) = | SaturWater_Enthalpy_t(t) | 1570.8785 | kJ/kg | x (p,s) = | SteamQuality_p_s(p,s) | 0.8 | - | K (p,h) = | H2O_Kappa_p_h(p,h) | 1.2903 | -
|  |  |  | x (t,s) = | SteamQuality_t_s(t,s) | 0.8 | - | KDown (p,h) = | H2O_KappaUp_p_h(p,h) | 1.2902 | -
s (t) = | SaturWater_Entropy_t(t) | 3.623 | kJ(kg K) |  |  |  |  | KUp (p,h) = | H2O_KappaDown_p_h(p,h) | 1.2903 | -
k (t) = | SaturWater_HeatConduct_t(t) | 0.47462 | W/(m K) |  |  |  |  | Pr (t,p) = | H2O_Prandtl_t_p(t,t) | 1.4279 | -
Pr (t) = | SaturWater_Prandtl_t(t) | 1.1824 | - |  |  |  |  | p (t,s) = | H2O_Pressure_t_s(t,s) | 140 | bar
c (t) = | SaturWater_SonicVelocity_t(t) | 682.8367 | m/s |  |  |  |  | p (t,v) = | H2O_Pressure_t_v(t,v) | 140 | bar
cp (t) = | SaturWater_SpecHeat_Cp_t(t) | 7.8117 | kJ/(kg K) |  |  |  |  | c (p,h) = | H2O_SonicVelocity_p_h(p,h) | 637.5455 | m/s
v (t) = | SaturWater_SpecVolume_t(t) | 0.0016097 | m3/kg |  |  |  |  | c (t,p) = | H2O_SonicVelocity_t_p(t,p) | 637.5458 | m/s
t (h) = | SaturWater_Temperature_h(h) | 336.6701 | ºC |  |  |  |  | Cp (t,p) = | H2O_SpecificHeat_Cp_t_p(t,p) | 2.7865
s (t) = | Water_SurfaceTension_t(t) | 0.0063167 | N/m |  |  |  |  | Cv (t,p) = | H2O_SpecificHeat_Cv_t_p(t,p) | 1.9309
[8 empty] | v (p,h) = | H2O_SpecVolume_p_h(p,h) | 0.022509
Saturated steam | [7 empty] | v (t,p) = | H2O_SpecVolume_p_h(t,p) | 0.022542 | m3/kg
m (t) = | SaturSteam_DynViscosity_t(t) | 2.2211e-05 | Pa s |  |  |  |  | t (p,h) = | H2O_Temperature_p_h(p,h) | 499.9995 | ºC
h (t) = | SaturSteam_Enthalpy_p(p) | 2638.0934 | kJ/kg |  |  |  |  | t (p,s) = | H2O_Temperature_p_s(p,s) | 500 | ºC
h (p) = | SaturSteam_Enthalpy_t(t) | 2638.0934 | kJ/kg | Note 1 | This set of functions uses Steamdat_97 . [3] |  |  | t (p,v) = | H2O_Temperature_p_v(p,v) | 499.9983 | ºC
s (p) = | SaturSteam_Entropy_p(p) | 5.373 | kJ/(kg K) |  | With permission (See sheet 6 )
s (t) = | SaturSteam_Entropy_t(t) | 5.373 | kJ/(kg K)
k (t) = | SaturSteam_HeatConduct_t(t) | 0.10471 | W/(m K) |  |  |  |  | The same functions are aplicable for compressed liquid
Pr (t) = | SaturSteam_Prandtl_t | 2.3885 | - |  |  |  |  | For the given pressure of p = |  | 140 | bar
c (t) = | SaturSteam_SonicVelocity_t(t) | 445.1849 | m/s |  |  |  |  | compressed liquid will exist for a temperature t < tsat
cp (t) = | SaturSteam_SpecHeat_Cp_t(t) | 11.2598 | kJ/(kg K) | [5 empty] | tsat = | 336.6414 | ºC
v (t) = | SaturSteam_SpecVolume_t(t) | 0.011489 | m3/kg

## 1.- Functions test
3043.1
Excel funtions "STEAMDAT_97" for Steam and Water Data
With permission (See sheet 6 )
Rev. cjc 01.06.2016
1.- Aplication case to superheated steam
(same functions are used for superheated steam and compressed water) |  |  |  | Aplication point is shown in water T-s diagram
Temperature |  |  | t = | 350 | ºC | psat,@t = | Non existing at this temperature
Pressure |  |  | p = | 61 | bar | tsat,@p = | H2O_SaturationTemp_p(G6) |  |  |  |  | t |  | pcrt = | 220.64 | bar
[6 empty] | tsat,@p = | 276.6299 | ºC | [7 empty] | p = | 61
Input data pair: |  |  |  | f(t,p) | f(t,s) | f(t,v) | f(p,s) | f(p,h) | f(p,v) |  | 350 |  | t = 350 ºC
Dynamic viscosity | Pa s | m = | H2O_DynViscosity_t_p(t,p) | 2.2102e-05 | [8 empty] | Tcrt = | 374 | ºC
Enthalpy | kJ/kg | h = | H2O_Enthalpy_t_p(t,p) | 3041.2313 | 3041.2296 |  | 3041.2337 |  |  |  | 300 | [5 empty] | 15.55
Entropy | kJ/kg.K | s= | H2O_Entropy_t_p(t,p) | 6.3246 |  |  |  | 6.3247
Heat conductivity | W/m.K | k = | H2O_HeatConductivity_t_p(t,p) | 0.057992
Kappa | - | K = | H2O_Kappa_t_p(t,p) | 1.2831 |  |  |  | 1.2839 |  |  | 200
Kappa-Down | - | Kdown = | H2O_KappaDown_p_h(p,h) | 1.2824 |  |  |  | 1.2824 | [9 empty] | 1
Kappa-Up | - | Kup = | H2O_KappaUp_p_h(p,h) | 1.2839 |  |  |  | 1.2839
Prandtl | - | Pr = | H2O_Prandtl_t_p(t,p) | 1.0942
Pressure | bar(a) |  |  |  | 61 | 60.9997 |  |  |  |  | 100
Sonic velocity | m/s | c = | H2O_SonicVelocity_t_p(t,p) | 569.621 | [12 empty] | s
Specific heat, Cp | kJ/kg.K | Cp = | H2O_SpecificHeat_Cp_t_p(t,p) | 2.871 | [8 empty] | Water t-s diagram
Specific volume | m3/kg | v = | H2O_SpecVolume_t_p(t,p) | 0.041454 |  |  |  | 0.041454
Surface tension | N/m | Surface tension is defined only in compressed liquid area
Temperature | °C | [5 empty] | 350 | 349.9997 | 350
[16 empty] | p = | 61
2.- Aplication case to compressed water | [10 empty] | 350
(same functions are used for superheated steam and compressed water) |  |  |  | Aplication point is shown in water T-s diagram | [8 empty] | Tcrt = | 374 | ºC
Temperature |  |  | t = | 200 | ºC | psat,@t = | 15.5488 | bar |  |  | 300 | [5 empty] | 15.5488
Pressure |  |  | p = | 61 | bar | tsat,@p = | 276.6299 | ºC
Input data pair: |  |  |  | f(t,p) | t-s | t-v | p-s | p-h | p-v |  | 200
Dynamic viscosity | Pa s | m = | H2O_DynViscosity_t_p(t,p) | 0.00013545 | [13 empty] | 1
Enthalpy | kJ/kg | h = | H2O_Enthalpy_t_p(t,p) | 854.2589 | 854.2658 |  | 854.2528
Entropy | kJ/kg.K | s= | H2O_Entropy_t_p(t,p) | 2.3237 |  |  |  | 2.3237
Heat conductivity | W/m.K | k = | H2O_HeatConductivity_t_p(t,p) | 0.66729 | [6 empty] | 100
Kappa | - | K = | H2O_Kappa_t_p(t,p) | 272.7296 |  |  |  | 272.7296 | [8 empty] | s
Kappa-Down | - | Kdown = | [5 empty] | 211.0035 |  |  |  |  | Water t-s diagram
Kappa-Up | - | Kup = | [5 empty] | 334.4557
Prandtl | - | Pr = | H2O_Prandtl_t_p(t,p) | 0.90698
Pressure | bar(a) |  |  |  | 61.0011
Sonic velocity | m/s | c = | H2O_SonicVelocity_t_p(t,p) | 1348.3413
Specific heat, Cp | kJ/kg.K | Cp = | H2O_SpecificHeat_Cp_t_p(t,p) | 3.3136
Specific volume | m3/kg | v = | H2O_SpecVolume_t_p(t,p) | 0.001152 |  |  |  | 0.001152
Surface tension | N/m |  | Water_SurfaceTension_t(G30) | 0.037684
Temperature | °C | [5 empty] | 200.0005 | 200 | 199.9948
3.- Application case to Wett steam
Input data for the example |  |  |  | Saturation Pressure Psat = |  | H2O_SaturationPressure_t(D56)
Temperature | 180 | ºC |  |  | Psat = | 10.0263 | bar
Steam quality | 0.6 | -
Pressure | 3.7755 | bar |  | Input data pair:
|  |  |  | t-x | t-s | p-x | p-h | p-s | p-v
Enthalpy | kJ/kg |  | H2O_Enthalpy_t_x(t,x) | 1971.6068 |  | 1971.6068 | - | 1971.6068
Entropy | kJ/kg.K |  | H2O_Entropy_p_h(p,h) |  | - |  | 4.8063 | -
Kappa | - | [5 empty] | 1.0685
Kappa-Down | - | [5 empty] | 1.0685
Kappa-Up | - | [5 empty] | 1.0684
Specific volume | m3/kg |  | H2O_SpecVolume_t_x(t,x) | 0.11677 |  | 0.11677 | 0.11677
Check example
Critical point |  |  |  | t = | 180 | ºC
Critical temperature: | 373.946 | °C |  | x = | 0.6 | -
Critical pressure: | 220.64 | bar(a)
|  |  |  | h = | hf + x * (hg - hf) |  |  | s = | sf + x * (sg - sf) |  |  | v = | vf + v * (vg - vf)
|  |  |  | hf = | SaturWater_Enthalpy_t(t) |  |  | sf = | SaturWater_Entropy_t(t) |  |  | vf = | SaturWater_SpecVolume_t(t)
|  |  |  | hf = | 763.188 | kJ/kg |  | sf = | 2.1395 | kJ/(kg*K) |  | vf = | 0.0011274 | m3/kg
|  |  |  | hg = | SaturSteam_Enthalpy_t(t) |  |  | sg = | SaturSteam_Entropy_t(t) |  |  | vg = | SaturSteam_SpecVolume_t(t)
|  |  |  | hg = | 2777.2194 | kJ/kg |  | sg = | 6.5841 | kJ/(kg*K) |  | vg = | 0.19386 | m3/kg
|  |  |  | x = | 0.6 |  |  | x = | 0.6 |  |  | x = | 0.6
|  |  |  | h = | 1971.6068 | kJ/kg |  | s = | 4.8063 | kJ/(kg*K) |  | v = | 0.11677 | m3/kg
t = 276.6 ºC
t = 276.6 ºC

## 2.- Turbine stage example
Rev. cjc 01.06.2016
Turbine stage
Input data is in yelow cells, calculated values in green cells
With permission (See sheet 5 ) | [5 empty] | t ºC
Input data: | [10 empty] | p1 = | 61 | bar
Steam pressure before stage | p1 = | 61 | bar(a)
Steam temperature before stage | t1 = | 450 | °C |  | 450 |  |  | 450
Pressure after stage | p2 = | 4.3 | bar(a)
Stage isentropic efficiency | hs = | 0.87 | - |  | 400
[8 empty] | pcrt = | 220.64 | bar
Calculated values:
Inlet enthalpy | h1 = | H2O_Enthalpy_t_p(t1,p1) | 3301.3191 | kJ/kg
Inlet entropy | s1 = | H2O_Entropy_t_p(t1,p1) | 6.7125 | kJ/kg.K | 300 |  | Tcrt = | 374 | ºC
Outlet isentropic entropy | s2s = | s1 | 6.7125 | kJ/kg.K
Outlet isentropic enthalpy | h2s = | H2O_Enthalpy_p_s(p2,s2s) | 2674.7741 | kJ/kg | [5 empty] | 276.667 | ºC
Isentropic power generation | Dhs = | h1 - h2s | 626.5449 | kJ/kg
Real power generation | Dh = | Dhs * hs | 545.0941 | kJ/kg | 200
Specific energy (Ditto) | Espec = | Dh [kJ/kg) * 1000 [kg/h] /3600 | 151.415 | kWh/ton | [8 empty] | 4.3 | bar
Outlet steam enthalpy | h2 = | h1 - Dh | 2756.225 | kJ/kg |  |  |  | 152.6418 | ºC
Outlet steam temperature | t2 = | H2O_Temperature_p_h(p2,h2) | 152.6418 | °C |  |  | t2sat = | 146.2383
Outlet saturation temperature | t2sat = | H2O_SaturationTemp_p(p2) | 146.2383 | °C | 100
Outlet steam superheating | Dtout,superheat = | t2 - t2sat = | 6.4035 | °C | [6 empty] | 6.7125 | 6.9064 |  | s kJ/(kg K)
Outlet steam entropy | s2 = | H2O_Entropy_p_h(p2,h2) | 6.9064 | kJ/kg.K |  |  | Water t-s diagram
2so
p2 =
1
2
Isentropic process
2sat
t1 =
ºC
t2 =
°C

## 3.- PRV example
Rev. cjc 01.06.2016
Desuperheating
Pump
Calculation of a pressure reducing valve, PRV, with desuperheating | [11 empty] | 3 |  |  | Feed water tank
Input data is in yellow cells. Water and steam properties calculated with "Steamdat_97" (Note 1) | [14 empty] | with saturated water
[11 empty] | 4 |  |  |  | at t3 ºC
Input data:
Steam pressure before PRV | p1 = | 62 | bar(a) |  |  |  |  | 1
Steam temperature before PRV | t1 = | 450 | °C
Steam pressure after PRV | p2 = | 4.3 | bar(a)
Steam temperature after PRV and desuperheating (2) | t2 = | 165 | -
Desuperheater water pressure | p4 = | 30 | bar(a) |  |  |  | 500 |  |  |  | Saturated vapor line
Desuperheater water temperature, in feed tank | t3 = | 130 | °C | [6 empty] | 450
Desuperheater water pump efficiency | hp = | 0.74 | - |  |  |  | 400
Pump motor efficiency | hm = | 0.94 | - | [6 empty] | 412.6473
High pressure steam flow | ms = | 75 | ton/h |  |  |  | 300
Note 1. With permission (See sheet 6 ) | [9 empty] | 277.7342
Note 2. Cooled, but still a superheated steam | [6 empty] | 200
165
Calculated data: | [6 empty] | 100 |  |  | 146.2383
Steam properties
Inlet steam entalpy | h1 = | H2O_Enthalpy_t_p(t1,p1) |  |  | 3299.8713 | kJ/kg | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Outlet steam enthalpy | h2 = | H2O_Enthalpy_t_p(t2,p2) |  |  | 2784.0309 | kJ/kg
Entropy at steam inlet conditions (p1, t1) | s1 = | H2O_Entropy_t_p(t1;p1) |  |  | 6.7035 | kJ/(kg*K) | 1: T; 6: Process 1 - 1a: Isentalpic pressure
Entropy at steam outlet conditions (p2, t2) | s2 = | H2O_Entropy_t_p(t2 ;p2) |  |  | 6.9708 | kJ/(kg*K) | 2: 130.4943; 6: reduction
Entropy at pressure "p1", in saturated condition | s1,sat = | SaturSteam_Entropy_p(p1) |  |  | 5.8744 | kJ/(kg*K) | 6: Process 1a - 2: Cooling of steam
Temperature at pressure "p1", in saturated condition | t1,sat = | H2O_SaturationTemp_p(p1) |  |  | 277.7342 | ºC | 2: 130; 6: with water
Saturated steam entropy at "p2" | s2,sat = | SaturSteam_Entropy_p(p2) |  |  | 6.8712 | kJ/(kg*K) | 6: Process 3 - 4: Water compresion
Saturated steam temperature at "p2" | t2,sat = | H2O_SaturationTemp_p(p2) |  |  | 146.2383 | ºC | 6: Process 4 - 2 (not shown), is the
Temperature after isentalpic expansion (h1) to "p2" | t1a = | H2O_Temperature_p_h(p2;h1) |  |  | 412.6473 | ºC | 6: heating and evaporation of the
cooling water flow mw.
Feed water tank with saturated water at t3
Desuperheater water enthalpy (in feed water tank) | h3 = | SaturWater_Enthalpy_t(t3) |  |  | 546.3878 | kJ/kg
Pressure in feed water tank | p3 = | H2O_SaturationPressure_t(t3) |  |  | 2.7026 | bar | bar: 5
Water entropy in feed water tank | s3 = | SaturWater_Entropy_t(t3) |  |  | 1.6346 | kJ/(kg*K) | 2: Pumping process
Feed water pump | [6 empty] | 0: Pump shaft power
Water entropy after pump, isentropic process | s4o = | s3 |  |  | 1.6346 | kJ/(kg*K) | 0: (The pump is calculated in the same way as a compressor would have been)
Isentropic outlet entalpy | h4o = | H2O_Enthalpy_p_s(p4,s4o) |  |  | 549.3135 | kJ/kg | 4: Pshaft =; 5: mw*Dh
Isentropic pump power demand: | Dhs = | h4o - h3 |  |  | 2.9257 | kJ/kg | 0: Feed water flow rate; 4: mw =; 5: 4.8112; 6: kg/s
Real pump specific power demand | [6 empty] | 0: Specific power demand for the water compresion; 4: Dh =; 5: 3.9536; 6: kJ/kg
Water pump efficiency | hp = | Dh / Dhs |  |  | 0.74 | - | 0: Pump shaft power; 4: Pshaft =; 5: mw*Dh
Specific power demand for the water compresion | Dh = | Dhs / hp |  |  | 3.9536 | kJ/kg | 4: Pshaft =; 5: 19.0217; 6: kW
Properties of desuperheating water, at PRV inlet (state "4") | [6 empty] | 0: Electrical pump power; 4: PElec =; 5: Pshaft / hm
Water outlet enthalpy | h4 = | h3 + Dh |  |  |  |  | 0: Pump shaft power; 4: Pshaft =; 5: 19.0217; 6: kW
| h3 = |  |  |  | 546.3878 |  | 0: Motor efficiency; 4: hm =; 5: 0.94; 6: -
| Dh = |  |  |  | 3.9536 |  | 0: Electrical pump power; 4: PElec =; 5: Pshaft /hm
| h4 = | h3 + Dh |  |  | 550.3415 | kJ/kg | 4: PElec =; 5: 20.2358; 6: kW
Water temperature at PRV inlet | t4 = | H2O_Temperature_p_h(p4,h4) |  |  | 130.4943 | ºC
Pump power can also be calculated as: (the normal way)
Energy balance |  | Ein = | Eout |  |  |  | 0: Water specific volume at inlet; 4: v =; 5: SaturWater_SpecVolume_t(t3)
[11 empty] | v = | 0.00107 | m3/kg
[7 empty] | Water density |  |  |  | rw = | 1 / v
[11 empty] | rw = | 934.5541 | kg/m3
[7 empty] | Water mass flow rate |  |  |  | mw = | ms * (h1 - h2) / (h2 - h4)
[11 empty] | mw = | 4.8112 | kg/s
[7 empty] | Water volume flow rate |  |  |  | Qw = | mw / rw
[11 empty] | Qw = | 0.0051481 | m3 /s
[7 empty] | Pump pressure increase |  |  |  | Dp = | p4 - p3
[11 empty] | Dp = | 27.2974 | bar
|  | ms * h1 + mw * h4 = | ms *h2 + mw * h2 |  |  |  | 0: Desuperheater water pump efficiency; 4: hp =; 5: 0.74; 6: -
|  | ms * (h1 - h2) = | mw * (h2 - h4) |  |  |  | 0: Pump shaft power; 4: Pshaft =; 5: Qw*Dp/hp
|  | mw = | ms * (h1 - h2) / (h2 - h4) |  |  |  | 4: Pshaft =; 5: 18.9905; 6: kW
[7 empty] | Motor efficiency |  |  |  | hm = | 0.94 | -
| Let | rh= | (h1 - h2) / (h2 - h4) |  |  |  | 0: Electrical pump power; 4: PElec =; 5: Pshaft / hm
|  | h1 = | 3299.8713 | kJ/kg |  |  | 4: PElec =; 5: 20.2027; 6: kW
|  | h2 = | 2784.0309 | kJ/kg
|  | h4 = | 550.3415 | kJ/kg
|  | rh= | 0.23094 | -
thus
|  | mw = | ms * rh
Required water per 1 kg of HP steam | mw,1 = | ms1 * rh
| ms1 = | 1 | kg s
| rh= | 0.23094 | -
| mw,1 = | 0.23094 | kg w / kg s
Water mass flow rate | mw = | ms * (h1 - h2) / (h2 - h4)
| mw = | ms * rh
| ms = | 75 | ton h
| ms = | 20.8333 | kg/s
| rh= | 0.23094 | -
| mw = | ms * rh
| mw = | 17.3202 | ton/h
| mw = | 4.8112 | kg/s
Low pressure steam flow rate | ms_LP = | ms + mw
| ms = | 20.8333 | kg/s
| mw = | 4.8112 | kg/s
| ms_LP = | 25.6445 | kg/s
| ms_LP = | 92.3202 | ton/h
3
4
s3 = s4o
4o
Saturated liquid line
PRV
p1, t1
p2, t2
ms
s
t
1
2
Steam
1a
2sat
t1,sat =
1sat
1a
h1 = const
mw
p3, t3
p2
p1
t1 =
t2 =
2
h1, p2
t2,sat =
t1a =
t3 =
t4 =
PRV
p1, t1
p2, t2
ms
Steam
1a
mw
p3, t3
2
h1, p2
1
3
4
Pump

## 4.- Dh
Enthalpy and temperature change in a compression process for a given pressure increment
Rev. cjc 01.06.2016
| For a compression |  |  | Thus |  |  | Units
| Pshaft = | mw*Dh |  | mw*Dh = | Qw*Dp/hp |  | Dh = | Dp/rw | [Pa * m3/kg ] |  | The actual change of enthalpy [J / kg] in a
| Pshaft = | Qw*Dp/hp |  | Qw*rw*Dh = | Qw*Dp/hp |  |  |  | [N/m2 * m3/kg ] |  | compression process is equivalent to the
|  |  |  | rw*Dh = | Dp/hp |  |  |  | [N * m/kg ] |  | pressure increment [Pa] divided by the
|  |  |  | Dh = | (Dp/rw)/hp |  |  |  | [J/kg ] |  | density [kg / m3] and the efficiency.
| Application |  |  |  |  | Pressure increment
| Fluid: | Water |  |  |  | DP = | 267 | ft wc |  | Power loss to the fluid
| Pressure |  |  |  |  | DP = | 81.3816 | mwc |  | DhLoss = | Dh * (1-hp)
| DP = | 267 | ft wc |  |  | DP = | 798080.8676 | Pa |  | Dh = | 1.3328 | kJ/kg
| Water density |  |  |  |  | DP = | 7.9808 | bar |  | hp = | 0.6
| rw = | 998 | kg/m³ | [6 empty] | DhLoss = | 0.53312 | kJ/kg
| Pump efficiency |  |  |  |  | Enthalpy change
| hp = | 0.6 | - |  |  | Dh = | (Dp/rw)/hp |  |  | Fluid temperature increment
| Water specific heat |  |  |  |  | DP = | 798080.8676 | Pa |  | Dh = | cp * Dt
| cp = | 4.182 | kJ/(kg * K) |  |  | rw = | 998 | kg/m³ |  | Dt = | Dh / cp
[6 empty] | hp = | 0.6 |  |  | Dh = | 0.53312 | kJ/kg
[6 empty] | Dh = | 1332.8004 | J/kg |  | cp = | 4.182 | kJ/(kg * K)
| g = | 9.8066 | m/s² |  |  | Dh = | 1.3328 | kJ/kg |  | Dt = | 0.12748 | K

## 5.- DP friction
Rev. cjc 01.06.2016
Pressure loss in steam pipe |  |  | Inside pipe diameter |  |  | Density |  |  | Reynolds number
|  |  | di = | Pipe_Imp_CS_Dint_dn_sch |  | r = | 1 / v |  | Re = | v * d / n
Saturated steam at pressure "Pg", in a |  |  | dn = | 10 | in | v = | 0.22033 | m³/Kg | v = | 34.6609 | m/s
locality with a height above sea level "H". |  |  | sch = | STD |  | r = | 4.5386 | kg/m³ | di = | 0.25446 | m
Carbon steel pipe with nominal diameter |  |  | di = | 254.46 | mm |  |  |  | n = | 3.2669e-06 | m²/s
"dn", schedule "sch" and absolute |  |  | di = | 0.25446 | m | Absolute viscosity |  |  | Re = | 2699719.5311 | -
rugosity "Rabs". | [5 empty] | m = | SaturSteam_DynViscosity_t
Steam mass flow rate "m". |  |  | Pipe section area |  |  | t = | 174.2403 | ºC | Friction factor
Pipe equivalent length "Leq". |  |  | A = | (p/4)*di^2 |  | m = | 1.4827e-05 | Pa s | f =
|  |  | di = | 0.25446 | m |  |  |  | Rrel = | 3.9299e-05 | -
Pg = | 8 | bar (g) | A = | 0.050854 | m² | Kinematic viscosity |  |  | Re = | 2699719.5311 | -
H = | 2300 | m.s.n.m. |  |  |  | n = | m / r |  | f = | 0.011244 | -
dn = | 10 | in | Relative rugosit |  |  | m = | 1.4827e-05 | Pa s
sch = | STD | - | Rrel = | Rabs / di |  | r = | 4.5386 | kg/m³ | Unit pressure loss
Rabs = | 0.01 | mm | Rabs = | 0.01 | mm | n = | 3.2669e-06 | m²/s | J = | f * (1 / di) * hv
m = | 8 | kg/s | di = | 254.46 | mm |  |  |  | f = | 0.011244 | -
Leq = | 500 | m | Rrel = | 3.9299e-05 | - | Volumetric flow rate |  |  | di = | 0.25446 | m
[6 empty] | V = | m / r |  | hv = | 2726.2826 | Pa
|  |  | Steam properties |  |  | m = | 8 | kg/s | J = | 120.4673 | Pa/m
Local atmospheric pressure |  |  | Entropy |  |  | r = | 4.5386 | kg/m³
Patm = 101,325* (1 -2,25577E-5 * H)^5,25588 |  |  | s = | SaturSteam_Entropy_p(H7) |  | V = | 1.7627 | m³/s | Pressure loss
H = | 2300 | m.a.s.l. | P = | 8.7658 | bar |  |  |  | DP = | J * Leq
patm = | 76.5784 | kPa | s = | 6.6303 | kJ/(kg*K) | Flow velocity (Note 1) |  |  | J = | 120.4673 | Pa/m
patm = | 0.76578 | bar |  |  |  | v = | V / A |  | J100m = | 0.12047 | bar / 100 m
|  |  | Temperature |  |  | V = | 1.7627 | m³/s | Leq = | 500 | m
Absolute pressure |  |  | t = | H2O_SaturationTemp_p(p) |  | A = | 0.050854 | m² | DP = | 60233.6344 | Pa
P = | patm + Pg |  | p = | 8.7658 | bar | v = | 34.6609 | m/s | DP = | 60.2336 | kPa
patm = | 0.76578 | bar | t = | 174.2403 | ºC | OK. Velocity within range |  |  | DP = | 0.60234 | bar
Pg = | 8 | barg
P = | 8.7658 | bar | Specific volume |  |  | Kinematic pressure |  |  | Pressure loss per 100 m
|  |  | v = | SaturSteam_SpecVolume_t |  | hv = | r / 2 * v^2 |  | DP100m = | 0.12047 | bar / 100 m
Note: Steamdat 97 is used [3] |  |  | t = | 174.2403 | ºC | r = | 4.5386 | kg/m³ | OK.Pressure loss within range
|  |  | v = | 0.22033 | m³/Kg | v = | 34.6609 | m/s
[6 empty] | hv = | 2726.2826 | Pa
Note (1) | According [2], for saturated steam with pressure in the range 1 to 7 bar (g),
the recommended velocity is in the range 10 to 38 m/s.
and the pressure drop in the range 0.11 to 0.34 bar / 100m

## 6.- Permission
To get "Steamdat" directly from ÂF
I am pleased to announce that Steamdat is now online again at ÅF external webpage.
Please find the add-in with installation instructions at
http://www.afconsult.com/en/do-business/your-industry/process-industry/steam-and-water-program-excel-addin/

## Ref. 2
http://www.watsonmcdaniel.com/2011Catalog/EngineeringData.pdf
Recommended velocities and pressure drops for |  |  |  |  | Recommended velocities and pressure drops for
various services [2] |  |  |  |  | various services [2]
Service | Velocity |  | Pressure drops |  | Service |  |  | Velocity |  | Pressure drops
| m/s |  | bar/100 m |  |  |  |  | ft/min |  | psi/100 ft
Saturated steam |  |  |  |  | Saturated steam
Vacuum | 10.16 | 20.32 | 0.056552 | 0.1131 | Vacuum |  |  | 2000 | 4000 | 0.25 | 0.5
0 - 1.03 bar (g) | 10.16 | 25.4 | 0.056552 | 0.1131 | 0 - 15 psig |  |  | 2000 | 5000 | 0.25 | 0.5
1.03 - 7 bar (g) | 10.16 | 38.1 | 0.1131 | 0.33931 | 15 - 100 psig |  |  | 2000 | 7500 | 0.5 | 1.5
Over 7 bar (g) | 10.16 | 45.72 | 0.1131 | 0.45241 | Over 100 psig |  |  | 2000 | 9000 | 0.5 | 2
Steam Main, Low noise | 20.32 | 30.48 |  |  | Steam Main, Low noise |  |  | 4000 | 6000
Steam Main, Industrial Plant | 40.64 | 60.96 |  |  | Steam Main, Industrial Plant |  |  | 8000 | 12000
Superheated Steam |  |  |  |  | Superheated Steam
0 - 7 bar (g) | 12.7 | 50.8 | 0.1131 | 0.33931 | 0- 100 psig |  |  | 2500 | 10000 | 0.5 | 1.5
7 - 35 bar (g) | 12.7 | 60.96 | 0.22621 | 0.45241 | 100 - 500 psig |  |  | 2500 | 12000 | 1 | 2
Condensate |  |  |  |  | Condensate |  |  | ft/sec
Boiler feed pump suction | 0.4572 | 0.762 |  |  | Boiler feed pump suction |  |  | 1.5 | 2.5
Condensate pump suction | 0.4572 | 0.9144 |  |  | Condensate pump suction |  |  | 1.5 | 3
Condensate pump discharge | 0.9144 | 2.286 |  |  | Condensate pump discharge |  |  | 3 | 7.5
Boiler feed pump discharge | 1.2192 | 3.048 |  |  | Boiler feed pump discharge |  |  | 4 | 10
Hot water (quiet flow) |  |  |  |  | Hot water (quiet flow) |  |  | ft/sec
Heating systems | 1.2192 |  |  |  | Heating systems |  |  | 4
Pump suction lines | 0.3048 | 2.4384 |  |  | Pump suction lines |  |  | 1 | 8
Pump discharge lines | 1.524 | 4.572 |  |  | Pump discharge lines |  |  | 5 | 15
Cooling water systems | 1.524 | 4.572 |  |  | Cooling water systems |  |  | 5 | 15
According [2], for saturated steam with pressure in the range 1 to 7 bar (g), |  |  |  |  | 1 ft/min = | 0.00508 | m/s | 1 psi /100 ft = | 0.068948 | bar/100 ft
the recommended velocity is in the range 10 to 38 m/s. |  |  |  |  | FtMin = | 0.00508 |  | 1 psi /100 ft = | 0.068948 | bar/30.48 m
and the pressure drop in the range 0.11 to 0.34 bar / 100m |  |  |  |  | 1 ft/sec = | 0.3048 |  | 1psi /100 ft = | 0.0022621 | bar/m
[5 empty] | FtSec = | 0.3048 |  | 1 psi /100 ft = | 0.22621 | bar/100 m
[8 empty] | PsiBar = | 0.22621

## Ref
[1] | AFCONSULT
Nygaard Johan
Delin Lennart [mailto:Lennart.Delin@afconsult.com]
[2] | Engineering Data
Watson McDaniel
http://www.watsonmcdaniel.com/2011Catalog/EngineeringData.pdf
[3] | Link to download the steam functions:
www.piping-tools.net
Steam. Steamdat functions. Link to free download

## Air Data (hidden)
-73.15 | 0.0181 | 1.007 | 0.737 | 1.7458 | 1.325e-05
-23.15 | 0.0223 | 1.006 | 0.72 | 1.3947 | 1.596e-05
26.85 | 0.0263 | 1.007 | 0.707 | 1.1614 | 1.846e-05
76.85 | 0.03 | 1.009 | 0.7 | 0.995 | 2.082e-05
126.85 | 0.0338 | 1.014 | 0.69 | 0.8711 | 2.301e-05
176.85 | 0.0373 | 1.021 | 0.686 | 0.774 | 2.507e-05
226.85 | 0.0407 | 1.03 | 0.684 | 0.6964 | 2.701e-05
276.85 | 0.0439 | 1.04 | 0.683 | 0.6329 | 2.884e-05
326.85 | 0.0469 | 1.051 | 0.685 | 0.5804 | 3.058e-05
376.85 | 0.0497 | 1.063 | 0.69 | 0.5356 | 3.225e-05
426.85 | 0.0524 | 1.075 | 0.695 | 0.4975 | 3.388e-05
476.85 | 0.0549 | 1.087 | 0.702 | 0.4643 | 3.546e-05
526.85 | 0.0573 | 1.099 | 0.709 | 0.4354 | 3.698e-05
576.85 | 0.0596 | 1.11 | 0.716 | 0.4097 | 3.843e-05
626.85 | 0.062 | 1.121 | 0.72 | 0.3868 | 3.981e-05
676.85 | 0.0643 | 1.131 | 0.723 | 0.3666 | 4.113e-05
726.85 | 0.0667 | 1.141 | 0.726 | 0.3482 | 4.244e-05
t | k | Cp | Pr | ragua | m
ºC | W/(m*K) | kJ/(kg*K) | - | kg/m3 | Pa s
Atmospheric air properties as a function of the temperature
Atmospheric air properties as a function
of the temperature
(Table A.4) | [1]

## Water Data (hidden)
0 | 0.569 | 4.217 | 12.99 | 1000 | 0.00175 | 1.75e-06 | 1.3493e-07 | 0.006108
1.85 | 0.574 | 4.211 | 12.22 | 1000 | 0.001652 | 1.652e-06 | 1.3631e-07 | 0.0069793
6.85 | 0.582 | 4.198 | 10.26 | 1000 | 0.001422 | 1.422e-06 | 1.3864e-07 | 0.0099092
11.85 | 0.59 | 4.189 | 8.81 | 1000 | 0.001225 | 1.225e-06 | 1.4085e-07 | 0.013876
16.85 | 0.598 | 4.184 | 7.56 | 999.001 | 0.00108 | 1.0811e-06 | 1.4307e-07 | 0.019178
21.85 | 0.606 | 4.181 | 6.62 | 998.004 | 0.000959 | 9.6092e-07 | 1.4523e-07 | 0.026181
26.85 | 0.613 | 4.179 | 5.83 | 997.009 | 0.000855 | 8.5756e-07 | 1.4713e-07 | 0.035323
31.85 | 0.62 | 4.178 | 5.2 | 995.0249 | 0.000769 | 7.7284e-07 | 1.4914e-07 | 0.047132
36.85 | 0.628 | 4.178 | 4.62 | 993.0487 | 0.000695 | 6.9986e-07 | 1.5136e-07 | 0.062228
41.85 | 0.634 | 4.179 | 4.16 | 991.0803 | 0.000631 | 6.3668e-07 | 1.5308e-07 | 0.081341
46.85 | 0.64 | 4.18 | 3.77 | 989.1197 | 0.000577 | 5.7758e-07 | 1.5326e-07 | 0.10532
51.85 | 0.645 | 4.182 | 3.42 | 987.1668 | 0.000528 | 5.3486e-07 | 1.5624e-07 | 0.13513
56.85 | 0.651 | 4.184 | 3.15 | 984.252 | 0.000489 | 4.9682e-07 | 1.5784e-07 | 0.1719
61.85 | 0.656 | 4.186 | 2.88 | 982.3183 | 0.000453 | 4.6115e-07 | 1.5953e-07 | 0.21689
66.85 | 0.66 | 4.188 | 2.66 | 979.4319 | 0.00042 | 4.2882e-07 | 1.609e-07 | 0.27153
71.85 | 0.664 | 4.191 | 2.45 | 976.5625 | 0.000389 | 3.9834e-07 | 1.6321e-07 | 0.33742
76.85 | 0.668 | 4.195 | 2.29 | 973.7098 | 0.000365 | 3.7485e-07 | 1.6354e-07 | 0.41632
81.85 | 0.671 | 4.199 | 2.14 | 970.8738 | 0.000343 | 3.5329e-07 | 1.6459e-07 | 0.51022
86.85 | 0.674 | 4.203 | 2.02 | 967.118 | 0.000324 | 3.3502e-07 | 1.6581e-07 | 0.62127
91.85 | 0.677 | 4.209 | 1.91 | 963.3911 | 0.000306 | 3.1763e-07 | 1.6696e-07 | 0.75183
96.85 | 0.679 | 4.214 | 1.8 | 960.6148 | 0.000289 | 3.0085e-07 | 1.6774e-07 | 0.90449
100 | 0.68 | 4.217 | 1.76 | 957.8544 | 0.000279 | 2.9128e-07 | 1.6835e-07 | 1.0133
t | k | Cp | Pr | ragua | m | n | a | Psat
ºC | W/(m*K) | kJ/(kg*K) | - | kg/m3 | Pa s | m2/s | m2/s | bar
Saturation properties of water as a function of the temperature
Saturated Water Properties as a Function
of Temperature (Table A.6) |  | [1]

## 6.CS_Imp (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2
3 | Pipe Thickness [mm], according ASME B36.10M
4
5 | [6 empty] | ASME B36.10M SCHEDULE / IDENTIFICATION | [9 empty] | Application |  | Dn = | 24 | mm
6 | Size | dext | 5 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | STD | XS | XXS | (with input validation) |  | SCH = | XS
7 | 0.5 | 21.3 | 1.65 | 2.11 | - | 2.41 | 2.77 | - | 3.73 | - | 0 | - | 4.78 | 2.77 | 3.73 | 7.47 | di = | Pipe_Imp_CS_Dint_dn_sch |  | #NAME? | mm
8 | 0.75 | 26.7 | 1.65 | 2.11 | - | 2.41 | 2.87 | - | 3.91 | - | 0 | - | 5.56 | 2.87 | 3.91 | 7.82 | de = | Pipe_Imp_CS_Dext_dn |  | #NAME? | mm
9 | 1 | 33.4 | 1.65 | 2.77 | - | 2.9 | 3.38 | - | 4.55 | - | 0 | - | 6.35 | 3.38 | 4.55 | 9.09 | s = | Pipe_Imp_CS_Thickness_dn_sch |  | #NAME? | mm
10 | 1.5 | 48.3 | 1.65 | 2.77 | - | 3.18 | 3.68 | - | 5.08 | - | 0 | - | 7.14 | 3.68 | 5.08 | 10.15
11 | 2 | 60.3 | 1.65 | 2.77 | - | 3.18 | 3.91 | - | 5.54 | - | 0 | - | 8.74 | 3.91 | 5.54 | 11.07 | Application |  | Dn = | 16 | mm
12 | 3 | 88.9 | 2.11 | 3.05 | - | 4.78 | 5.49 | - | 7.62 | - | 0 | - | 11.13 | 5.49 | 7.62 | 15.24 | (without input validation) |  | SCH = | 81
13 | 4 | 114.3 | 2.11 | 3.05 | - | 4.78 | 6.02 | - | 8.56 | - | 11.13 | - | 13.49 | 6.02 | 8.56 | 17.12 | di = | Pipe_Imp_CS_Dint_dn_sch |  | #NAME? | mm
14 | 5 | 141.3 | 2.77 | 3.4 | - | - | 6.55 | - | 9.53 | - | 12.7 | - | 15.88 | 6.55 | 9.53 | 19.05 | de = | Pipe_Imp_CS_Dext_dn |  | #NAME? | mm
15 | 6 | 168.3 | 2.77 | 3.4 | - | - | 7.11 | - | 10.97 | - | 14.27 | - | 18.26 | 7.11 | 10.97 | 21.95 | s = | Pipe_Imp_CS_Thickness_dn_sch |  | #NAME? | mm
16 | 8 | 219.1 | 2.77 | 3.76 | 6.35 | 7.04 | 8.18 | 10.31 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01 | 8.18 | 12.7 | 22.23 | The shedule entered is wrong
17 | 10 | 273 | 3.4 | 4.19 | 6.35 | 7.8 | 9.27 | 12.7 | 15.09 | 18.26 | 21.44 | 25.4 | 28.58 | 9.27 | 12.7 | 25.4
18 | 12 | 323.8 | 3.96 | 4.57 | 6.35 | 8.38 | 10.31 | 14.27 | 17.48 | 21.44 | 25.4 | 28.58 | 33.32 | 9.53 | 12.7 | 25.4
19 | 14 | 355.6 | 3.96 | 6.35 | 7.92 | 9.53 | 11.13 | 15.09 | 19.05 | 23.83 | 27.79 | 31.75 | 35.71 | 9.53 | 12.7 | -
20 | 16 | 406.4 | 4.19 | 6.35 | 7.92 | 9.53 | 12.7 | 16.66 | 21.44 | 26.19 | 30.96 | 36.53 | 40.49 | 9.53 | 12.7 | -
21 | 18 | 457 | 4.19 | 6.35 | 7.92 | 11.13 | 14.27 | 19.05 | 23.83 | 29.36 | 34.93 | 39.67 | 45.24 | 9.53 | 12.7 | -
22 | 20 | 508 | 4.78 | 6.35 | 9.53 | 12.7 | 15.09 | 20.62 | 26.19 | 32.54 | 38.1 | 44.45 | 50.01 | 9.53 | 12.7 | -
23 | 22 | 559 | 4.78 | 6.35 | 9.53 | 12.7 | - | 22.23 | 28.58 | 34.93 | 41.28 | 47.63 | 53.98 | 9.53 | 12.7 | -
24 | 24 | 610 | 5.54 | 6.35 | 9.53 | 14.27 | 17.48 | 24.61 | 30.96 | 38.89 | 46.02 | 52.37 | 59.54 | 9.53 | 12.7 | -
25 | 26 | 660 | - | 7.92 | 12.7 | 15.88 | - | - | - | - | - | - | - | 9.53 | 12.7 | -
26 | 28 | 711 | - | 7.92 | 12.7 | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
27 | 30 | 762 | 6.35 | 7.92 | 12.7 | 15.88 | - | - | - | - | - | - | - | 9.53 | 12.7 | -
28 | 32 | 813 | - | 7.92 | 12.7 | 15.88 | 17.48 | - | - | - | - | - | - | 9.53 | 12.7 | -
29 | 34 | 864 | - | 7.92 | 12.7 | 15.88 | 17.48 | - | - | - | - | - | - | 9.53 | 12.7 | -
30 | 36 | 914 | - | 7.92 | 12.7 | 15.88 | 19.05 | - | - | - | - | - | - | 9.53 | 12.7 | -
31 | 38 | 965 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
32 | 40 | 1016 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
33 | 42 | 1067 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
34 | 44 | 1118 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
35 | 46 | 1168 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
36 | 48 | 1219 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
'PipeImp_CS_Dext_dn
'The function PipeImp_CS_Dext_dn gives the exterior diameter of a pipe with
'nominal diameter dn [in]
'If the diameter is a fraction, the input cell has to be formated as a fraction
Function PipeImp_CS_Dext_dn(Dn)
Dim msg As String
Dim C(36, 3) As Variant
Mensaje = "NO"
' Exterior diameters according ASME B36.10M, from Sheet 6.CS_Imp, 3th column
For m = 1 To 36
C(m, 3) = ThisWorkbook.Worksheets("6.CS_Imp").Cells(m, 3).Value
Next m
' The corresponding line of the matrix C is asigned to its Dn-value
If Dn = 0.5 Then
x = 7
ElseIf Dn = 0.75 Then x = 8
ElseIf Dn = 1 Then x = 9
ElseIf Dn = 1.5 Then x = 10
ElseIf Dn = 2 Then x = 11
ElseIf Dn = 3 Then x = 12
ElseIf Dn = 4 Then x = 13
ElseIf Dn = 5 Then x = 14
ElseIf Dn = 6 Then x = 15
ElseIf Dn = 8 Then x = 16
ElseIf Dn = 10 Then x = 17
ElseIf Dn = 12 Then x = 18
ElseIf Dn = 14 Then x = 19
ElseIf Dn = 16 Then x = 20
ElseIf Dn = 18 Then x = 21
ElseIf Dn = 20 Then x = 22
ElseIf Dn = 22 Then x = 23
ElseIf Dn = 24 Then x = 24
ElseIf Dn = 26 Then x = 26
ElseIf Dn = 28 Then x = 26
ElseIf Dn = 30 Then x = 27
ElseIf Dn = 32 Then x = 28
ElseIf Dn = 34 Then x = 29
ElseIf Dn = 36 Then x = 30
ElseIf Dn = 38 Then x = 31
ElseIf Dn = 40 Then x = 32
ElseIf Dn = 42 Then x = 33
ElseIf Dn = 44 Then x = 34
ElseIf Dn = 46 Then x = 35
ElseIf Dn = 48 Then x = 36
' If the Dn-value is not within the given values,
' The function returns Dext = "N/A"
Else
PipeImp_CS_Dext_dn = "N/A"
Exit Function
End If
' In case the input value for Dn was identified and therefore an x-value "x" has been defined,
' the value of the matrix element (x,3) is assigned to de exterior diameter Dext
PipeImp_CS_Dext_dn = C(x, 3)
End Function
'PipeImp_CS_Thickness_dn_sch
'The function PipeImp_CS_Thickness_dn_sch gives the thickness of a pipe with
'nominal diameter dn [in] and schedule sch
'If the diameter is a fraction, the input cell ha to be formated as a fraction
Function PipeImp_CS_Thickness_dn_sch(Dn, SCH)
Dim C(36, 17) As Variant
' Thickness according ASME B36.10M, from Sheet 6.CS_Imp
For m = 1 To 36
For j = 1 To 17
C(m, j) = ThisWorkbook.Worksheets("6.CS_Imp").Cells(m, j).Value
Next j
Next m
If PipeImp_CS_Dext_dn(Dn) = "N/A" Then
PipeImp_CS_Thickness_dn_sch = "N/A"
Exit Function
End If
If Dn = 0.5 Then
x = 7
ElseIf Dn = 0.75 Then x = 8
ElseIf Dn = 1 Then x = 9
ElseIf Dn = 1.5 Then x = 10
ElseIf Dn = 2 Then x = 11
ElseIf Dn = 3 Then x = 12
ElseIf Dn = 4 Then x = 13
ElseIf Dn = 5 Then x = 14
ElseIf Dn = 6 Then x = 15
ElseIf Dn = 8 Then x = 16
ElseIf Dn = 10 Then x = 17
ElseIf Dn = 12 Then x = 18
ElseIf Dn = 14 Then x = 19
ElseIf Dn = 16 Then x = 20
ElseIf Dn = 18 Then x = 21
ElseIf Dn = 20 Then x = 22
ElseIf Dn = 22 Then x = 23
ElseIf Dn = 24 Then x = 24
ElseIf Dn = 26 Then x = 26
ElseIf Dn = 28 Then x = 26
ElseIf Dn = 30 Then x = 27
ElseIf Dn = 32 Then x = 28
ElseIf Dn = 34 Then x = 29
ElseIf Dn = 36 Then x = 30
ElseIf Dn = 38 Then x = 31
ElseIf Dn = 40 Then x = 32
ElseIf Dn = 42 Then x = 33
ElseIf Dn = 44 Then x = 34
ElseIf Dn = 46 Then x = 35
ElseIf Dn = 48 Then x = 36
Else
PipeImp_CS_Thickness_dn_sch(Dn, SCH) = "N/A"
Exit Function
End If
If SCH = 5 Then
Y = 4
ElseIf SCH = 10 Then Y = 5
ElseIf SCH = 20 Then Y = 6
ElseIf SCH = 30 Then Y = 7
ElseIf SCH = 40 Then Y = 8
ElseIf SCH = 60 Then Y = 9
ElseIf SCH = 80 Then Y = 10
ElseIf SCH = 100 Then Y = 11
ElseIf SCH = 120 Then Y = 12
ElseIf SCH = 140 Then Y = 13
ElseIf SCH = 160 Then Y = 14
ElseIf SCH = "STD" Then Y = 15
ElseIf SCH = "XS" Then Y = 16
ElseIf SCH = "XXS" Then Y = 17
Else
PipeImp_CS_Thickness_dn_sch = "N/A"
Exit Function
End If
PipeImp_CS_Thickness_dn_sch = C(x, Y)
If PipeImp_CS_Thickness_dn_sch = " - " Then
PipeImp_CS_Thickness_dn_sch = "N/A"
End If
End Function
'PipeImp_CS_Dint_dn_sch
'The function PipeImp_CS_Dint_dn_sch gives the interior diameter of a pipe with
'nominal diameter dn [in] and schedule sch
'If the diameter is a fraction, the input cell ha to be formated as a fraction
Function PipeImp_CS_Dint_dn_sch(Dn, SCH)
If PipeImp_CS_Thickness_dn_sch(Dn, SCH) = "N/A" Then
PipeImp_CS_Dint_dn_sch = "N/A"
Exit Function
End If
If PipeImp_CS_Dext_dn(Dn) = "N/A" Then
PipeImp_CS_Dint_dn_sch = "N/A"
Exit Function
End If
PipeImp_CS_Dint_dn_sch = PipeImp_CS_Dext_dn(Dn) - PipeImp_CS_Thickness_dn_sch(Dn, SCH) * 2
End Function

## Table-3-1 (hidden)
1 | 0 | -2 | 0.14633
2 | 0 | -1 | -0.84548
3 | 0 | 0 | -3.7564
4 | 0 | 1 | 3.3855
5 | 0 | 2 | -0.95792
6 | 0 | 3 | 0.15772
7 | 0 | 4 | -0.016616
8 | 0 | 5 | 0.00081215
9 | 1 | -9 | 0.00028319
10 | 1 | -7 | -0.00060706
11 | 1 | -1 | -0.01899
12 | 1 | 0 | -0.03253
13 | 1 | 1 | -0.021842
14 | 1 | 3 | -5.2838e-05
15 | 2 | -3 | -0.00047184
16 | 2 | 0 | -0.00030002
17 | 2 | 1 | 4.7661e-05
18 | 2 | 3 | -4.4142e-06
19 | 2 | 17 | -7.2695e-16
20 | 3 | -4 | -3.168e-05
21 | 3 | 0 | -2.8271e-06
22 | 3 | 6 | -8.5205e-10
23 | 4 | -5 | -2.2425e-06
24 | 4 | -2 | -6.5171e-07
25 | 4 | 10 | -1.4342e-13
26 | 5 | -8 | -4.0517e-07
27 | 8 | -11 | -1.2734e-09
28 | 8 | -6 | -1.7425e-10
29 | 21 | -29 | -6.8762e-19
30 | 23 | -31 | 1.4478e-20
31 | 29 | -38 | 2.6336e-23
32 | 30 | -39 | -1.1948e-23
33 | 31 | -40 | 1.8228e-24
34 | 32 | -41 | -9.3537e-26
i | I1 | J1 | n1
Table 3.1. Coefficients and exponents of Eq. (3.1)

## Table-3-9 (hidden)
1 | 348.0519
2 | -1.1672
3 | 0.0010193
4 | 572.5446
5 | 13.9188
Table 3.9. Coefficients of Eqs. (3.6) and (3.7)

## Table-3-10 (hidden)
1 | 0 | -9.6928
2 | 1 | 10.0867
3 | -5 | -0.0056088
4 | -4 | 0.071453
5 | -3 | -0.4071
6 | -2 | 1.4241
7 | -1 | -4.384
8 | 2 | -0.28409
9 | 3 | 0.021268
Table 3.10. Coefficients and exponents of Eq. (3.9)a

## Table-3-11 (hidden)
1 | 1 | 0 | -0.0017732
2 | 1 | 1 | -0.017835
3 | 1 | 2 | -0.045996
4 | 1 | 3 | -0.057581
5 | 1 | 6 | -0.050325
6 | 2 | 1 | -3.3033e-05
7 | 2 | 2 | -0.00018949
8 | 2 | 4 | -0.0039393
9 | 2 | 7 | -0.043797
10 | 2 | 36 | -2.6675e-05
11 | 3 | 0 | 2.0482e-08
12 | 3 | 1 | 4.3871e-07
13 | 3 | 3 | -3.2278e-05
14 | 3 | 6 | -0.0015034
15 | 3 | 35 | -0.040668
16 | 4 | 1 | -7.8847e-10
17 | 4 | 2 | 1.2791e-08
18 | 4 | 3 | 4.8225e-07
19 | 5 | 7 | 2.2922e-06
20 | 6 | 3 | -1.6715e-11
21 | 6 | 16 | -0.0021171
22 | 6 | 35 | -23.8957
23 | 7 | 0 | -5.906e-18
24 | 7 | 11 | -1.2622e-06
25 | 7 | 25 | -0.038947
26 | 8 | 8 | 1.1256e-11
27 | 8 | 36 | -8.2311
28 | 9 | 13 | 1.981e-08
29 | 10 | 4 | 1.0407e-19
30 | 10 | 10 | -1.0235e-13
31 | 10 | 14 | -1.0018e-09
32 | 16 | 29 | -8.0883e-11
33 | 16 | 50 | 0.10693
34 | 18 | 57 | -0.33662
35 | 20 | 20 | 8.9186e-25
36 | 20 | 35 | 3.0629e-13
37 | 20 | 48 | -4.2002e-06
38 | 21 | 21 | -5.9056e-26
39 | 22 | 53 | 3.7827e-06
40 | 23 | 39 | -1.2769e-15
41 | 24 | 26 | 7.3088e-29
42 | 24 | 40 | 5.5415e-17
43 | 24 | 58 | -9.437e-07
i | I2 | J2 | n2
Table 3.11. Coefficients and exponents of Eq. (3.10)

## Table-3-16 (hidden)
1 | 1 | 0 | -0.0073362
2 | 1 | 2 | -0.088224
3 | 1 | 5 | -0.072335
4 | 1 | 11 | -0.0040813
5 | 2 | 1 | 0.0020098
6 | 2 | 7 | -0.053046
7 | 2 | 16 | -0.007619
8 | 3 | 4 | -0.0063498
9 | 3 | 16 | -0.086043
10 | 4 | 7 | 0.0075322
11 | 4 | 10 | -0.0079238
12 | 5 | 9 | -0.00022888
13 | 5 | 10 | -0.0026457
Table 3.16. Coefficients and exponents of Eq. (3.12)

## Table-3-30 (hidden)
1 | 0 | 0 | 1.0658
2 | 0 | 0 | -15.7328
3 | 0 | 1 | 20.9444
4 | 0 | 2 | -7.6868
5 | 0 | 7 | 2.6186
6 | 0 | 10 | -2.8081
7 | 0 | 12 | 1.2053
8 | 0 | 23 | -0.0084567
9 | 1 | 2 | -1.2654
10 | 1 | 6 | -1.1524
11 | 1 | 15 | 0.88521
12 | 1 | 17 | -0.64208
13 | 2 | 0 | 0.38493
14 | 2 | 2 | -0.85215
15 | 2 | 6 | 4.8972
16 | 2 | 7 | -3.0503
17 | 2 | 22 | 0.039421
18 | 2 | 26 | 0.12558
19 | 3 | 0 | -0.27999
20 | 3 | 2 | 1.39
21 | 3 | 4 | -2.019
22 | 3 | 16 | -0.0082148
23 | 3 | 26 | -0.47596
24 | 4 | 0 | 0.043984
25 | 4 | 2 | -0.44476
26 | 4 | 4 | 0.90572
27 | 4 | 26 | 0.70522
28 | 5 | 1 | 0.10771
29 | 5 | 3 | -0.32914
30 | 5 | 26 | -0.50871
31 | 6 | 0 | -0.022175
32 | 6 | 2 | 0.094261
33 | 6 | 26 | 0.16436
34 | 7 | 2 | -0.013503
35 | 8 | 26 | -0.014834
36 | 9 | 2 | 0.00057923
37 | 9 | 26 | 0.0032309
38 | 10 | 0 | 8.0965e-05
39 | 10 | 1 | -0.00016558
40 | 11 | 26 | -4.4924e-05
i | I | J | n
Table 3.30. Coefficients and exponents of Eq. (3.21)

## Table-3-34 (hidden)
1 | 1167.0521
2 | -724213.167
3 | -17.0738
4 | 12020.8247
5 | -3232555.0322
6 | 14.9151
7 | -4823.2657
8 | 405113.4054
9 | -0.23856
10 | 650.1753
Table 3.34. Coefficients of Eqs. (3.22) to (3.24)

## Table-4-2 (hidden)
1 | 0 | 0 | 0.5132
2 | 0 | 1 | 0.32057
3 | 0 | 4 | -0.77826
4 | 0 | 5 | 0.18854
5 | 1 | 0 | 0.21518
6 | 1 | 1 | 0.73179
7 | 1 | 2 | 1.241
8 | 1 | 3 | 1.4768
9 | 2 | 0 | -0.28181
10 | 2 | 1 | -1.0708
11 | 2 | 2 | -1.2632
12 | 3 | 0 | 0.17781
13 | 3 | 1 | 0.4605
14 | 3 | 2 | 0.23404
15 | 3 | 3 | -0.49242
16 | 4 | 0 | -0.041766
17 | 4 | 3 | 0.16004
18 | 5 | 1 | -0.015784
19 | 6 | 3 | -0.0036295
i | I | J | n

## Fysikalkonstanter (hidden)
0.50194
0.16289
-0.13036
0.90792
-0.55112
0.14654
0.23562
0.78939
0.67366
1.2076
0.067067
-0.084337
-0.27464
-0.74354
-0.95946
-0.68734
-0.49709
0.19529
0.14583
0.26313
0.34725
0.21349
0.10075
-0.032932
-0.027045
-0.025309
-0.026776
-0.08229
0.060225
-0.020259

## Lambda (hidden)
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
ln(p) | 0 | 50 | 70 | 100 | 120 | 150 | 170 | 200 | 220 | 250 | 270 | 300 | 320 | 350 | 370 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 740 | 800
-4.6052 | 0.96944 | 1.0049 | 1.0109 | 1.0144 | 1.0151 | 1.0142 | 1.0131 | 1.0106 | 1.0092 | 1.0069 | 0.99871 | 1.0036 | 1.0025 | 1.0012 | 1.0006 | 0.99976 | 0.99909 | 0.99918 | 0.99959 | 1.0004 | 1.0014 | 1.0023 | 1.0031 | 1.004 | 0 | 0.01
-2.3026 | 0.97095 | 0.99781 | 1.0053 | 1.0109 | 1.0125 | 1.0125 | 1.0118 | 1.01 | 1.0086 | 1.0066 | 0.99399 | 1.0033 | 1.0024 | 1.0012 | 1.0005 | 0.99971 | 0.99919 | 0.99912 | 0.99967 | 1.0005 | 1.0014 | 1.0024 | 1.0032 | 1.004 | 1 | 0.1
-0.69315 | 1 | 1 | 0.9908 | 0.9981 | 1.0023 | 1.0058 | 1.0068 | 1.0066 | 1.0062 | 1.005 | 1.0041 | 1.0028 | 1.0018 | 1.0008 | 1.0003 | 0.99971 | 0.99916 | 0.99921 | 0.99959 | 1.0004 | 1.0013 | 1.0024 | 1.0031 | 1.004 | 2 | 0.5
0 | 1 | 1 | 1.0046 | 0.98837 | 0.99277 | 0.99824 | 1.001 | 1.003 | 1.0034 | 1.0033 | 1.0026 | 1.002 | 1.0013 | 1.0004 | 0.99995 | 0.99949 | 0.99909 | 0.9991 | 0.99961 | 1.0004 | 1.0014 | 1.0024 | 1.0031 | 1.004 | 3 | 1
1.6094 | 1 | 1 | 1 | 1 | 1 | 0.97397 | 0.97417 | 0.98065 | 0.98539 | 0.99094 | 0.99351 | 0.996 | 0.99692 | 0.99777 | 0.99807 | 0.99829 | 0.99856 | 0.99892 | 0.99961 | 1.0003 | 1.0013 | 1.0023 | 1.003 | 1.0039 | 4 | 5
2.3026 | 1 | 1 | 1 | 1 | 1 | 1 | 0.97331 | 0.96926 | 0.97243 | 0.97997 | 0.98469 | 0.98991 | 0.99238 | 0.99487 | 0.99605 | 0.99706 | 0.99811 | 0.99881 | 0.99946 | 1.0003 | 1.0011 | 1.0021 | 1.0029 | 1.0039 | 5 | 10
2.9957 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.97696 | 0.97114 | 0.97508 | 0.98202 | 0.98594 | 0.99054 | 0.99249 | 0.99509 | 0.99738 | 0.99856 | 0.9993 | 0.99996 | 1.0008 | 1.0017 | 1.0025 | 1.0037 | 6 | 20
3.912 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0246 | 1.0011 | 0.98526 | 0.98413 | 0.98651 | 0.9871 | 0.9914 | 0.99585 | 0.998 | 0.99877 | 0.999 | 0.99929 | 0.99991 | 1.0008 | 1.0024 | 7 | 50
4.2485 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0419 | 1.0076 | 0.996 | 0.99101 | 0.98715 | 0.99061 | 0.99514 | 0.99749 | 0.99813 | 0.99787 | 0.99778 | 0.99827 | 0.99915 | 1.0011 | 8 | 70
4.6052 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0409 | 1.0259 | 1.0072 | 0.99232 | 0.99079 | 0.9941 | 0.99662 | 0.99678 | 0.99588 | 0.99512 | 0.99704 | 0.99607 | 0.99842 | 9 | 100
5.0106 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.92309 | 1.0338 | 1.017 | 0.99052 | 0.9915 | 0.99455 | 0.99397 | 0.99155 | 0.98946 | 0.98694 | 0.98943 | 0.99228 | 10 | 150
5.2983 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.52547 | 1.083 | 0.97905 | 0.98553 | 0.99137 | 0.99053 | 0.98641 | 0.98264 | 0.98099 | 0.98147 | 0.98457 | 11 | 200
5.3936 | 1.0031 | 0.99695 | 0.99571 | 0.99823 | 1.0004 | 1.0021 | 1.0019 | 0.99984 | 0.99783 | 0.9949 | 0.99388 | 0.99493 | 0.99581 | 0.98328 | 0.63187 | 0.96833 | 0.98188 | 0.98987 | 0.98896 | 0.98422 | 0.97978 | 0.97763 | 0.97798 | 0.98118 | 12 | 220
5.4381 | 1.0032 | 0.99699 | 0.99573 | 0.99821 | 1.0004 | 1.0021 | 1.0018 | 0.99979 | 0.99779 | 0.99489 | 0.99385 | 0.99486 | 0.99584 | 0.98427 | 0.95503 | 0.96187 | 0.97969 | 0.98906 | 0.98827 | 0.98313 | 0.97828 | 0.97594 | 0.97614 | 0.97944 | 13 | 230
6.2146 | 1.004 | 0.99796 | 0.99588 | 0.99734 | 0.9989 | 0.9999 | 0.99943 | 0.99747 | 0.99585 | 0.99353 | 0.99262 | 0.99312 | 0.99474 | 0.99569 | 0.99027 | 0.97102 | 1.0001 | 1.0118 | 0.99406 | 0.97069 | 0.94981 | 0.93653 | 0.93174 | 0.93248 | 14 | 500
6.5511 | 1.0047 | 0.99829 | 0.99564 | 0.99631 | 0.99738 | 0.99771 | 0.99696 | 0.9949 | 0.99338 | 0.99149 | 0.99088 | 0.99157 | 0.99333 | 0.9968 | 0.99726 | 0.99053 | 0.98201 | 1.0323 | 1.0423 | 1.0051 | 0.96547 | 0.93749 | 0.92443 | 0.91737 | 15 | 700
6.9078 | 1.0066 | 0.99851 | 0.995 | 0.99443 | 0.99465 | 0.99377 | 0.99237 | 0.9898 | 0.9883 | 0.98694 | 0.98689 | 0.9884 | 0.99064 | 0.99574 | 0.99957 | 1.0035 | 1.0036 | 1.0244 | 1.0666 | 1.0719 | 1.0373 | 0.99564 | 0.96941 | 0.94566 | 16 | 1000

## Saturconstants (hidden)
1.8541 | 0.00048363 | 6.6961e-06 | -5.8899e-08 | 2.9089e-09 | -2.9894e-11 | 1.6939e-13 | -4.9703e-16 | 5.9702e-19 | Satur Steam spec heat
3.772 | 0.031571 | -0.0012265 | 0.00012375 | -5.2329e-06 | 1.2414e-07 | -1.6292e-09 | 1.1048e-11 | -2.9488e-14 | Satur Steam spec heat
17.15 | 0.797 | 4.18e-25 | [6 empty] | Satur Steam spec heat
4.2169 | -0.0033009 | 0.00010818 | -1.8289e-06 | 1.8711e-08 | -1.1209e-10 | 3.9618e-13 | -7.6649e-16 | 6.3738e-19 | Satur Water spec heat
4.867 | 0.0088032 | 0.00051288 | -3.6016e-05 | 1.598e-06 | -3.8219e-08 | 5.1797e-10 | -3.6997e-12 | 1.0965e-14 | Satur Water spec heat
10.11 | 0.447 | 2.3003e-25 | [6 empty] | Satur Water spec heat
8.8328 | 0.039019 | -0.00042952 | 1.1599e-05 | -1.3394e-07 | 7.5945e-10 | -2.0953e-12 | 2.2562e-15 | 0
17.5691 | 0.032647 | -0.0025664 | 0.00020713 | -6.8988e-06 | 1.2296e-07 | -1.1867e-09 | 5.758e-12 | -1.0732e-14
29.72 | 0.1125 | 0.51125
0.00055804 | 1.9612e-05 | 1.2022e-07 | -2.6656e-10 | 1.1655e-11 | -2.4401e-13 | 1.9915e-15 | -7.2686e-18 | 9.8815e-21
106.4964 | -0.40543 | -0.0015892 | 7.3563e-05 | -1.5144e-06 | 1.4066e-08 | -4.2449e-11 | -5.3442e-14 | 0
52.16 | -0.3525 | -0.44875
0.017068 | 0.0055287 | 1.2673e-05 | 0.0090937 | -0.014679 | 0.012764 | -0.0059541 | 0.0014117 | -0.000133 | Steam heat conductivity 0 - 250 °C
-461.4818 | 989.9343 | -838.121 | 323.4338 | -26.6775 | -24.3635 | 9.7428 | -1.5098 | 0.08882 | Steam heat conductivity 250 - 360 °C
Steam heat conductivity >360, in the module
0.56022 | 0.19647 | 0.013067 | -0.24058 | 0.24519 | -0.12661 | 0.036755 | -0.005783 | 0.00038622 | Water heat conductivity 0 - 366 °C
Water heat conductivity >366, in the module
0.97884 | 0.0013932 | -0.0001079 | 2.7045e-06 | -3.062e-08 | 1.8193e-10 | -5.7663e-13 | 9.1363e-16 | -5.6238e-19
0.074645 | 0.0030769 | 1.3104e-05 | 3.476e-07 | -4.8716e-09 | 2.1214e-11 | 1.277e-14 | -3.5596e-16 | 7.2175e-19
5.387 | 3.2069 | 8.5748e-29
7.802 | 4.338 | 1.3786e-28