## Air Data (hidden)
-73.15 | 0.0181 | 1.007 | 0.737 | 1.7458 | 1.325e-05
-23.15 | 0.0223 | 1.006 | 0.72 | 1.3947 | 1.596e-05
26.85 | 0.0263 | 1.007 | 0.707 | 1.1614 | 1.846e-05
76.85 | 0.03 | 1.009 | 0.7 | 0.995 | 2.082e-05
126.85 | 0.0338 | 1.014 | 0.69 | 0.8711 | 2.301e-05
176.85 | 0.0373 | 1.021 | 0.686 | 0.774 | 2.507e-05
226.85 | 0.0407 | 1.03 | 0.684 | 0.6964 | 2.701e-05
276.85 | 0.0439 | 1.04 | 0.683 | 0.6329 | 2.884e-05
326.85 | 0.0469 | 1.051 | 0.685 | 0.5804 | 3.058e-05
376.85 | 0.0497 | 1.063 | 0.69 | 0.5356 | 3.225e-05
426.85 | 0.0524 | 1.075 | 0.695 | 0.4975 | 3.388e-05
476.85 | 0.0549 | 1.087 | 0.702 | 0.4643 | 3.546e-05
526.85 | 0.0573 | 1.099 | 0.709 | 0.4354 | 3.698e-05
576.85 | 0.0596 | 1.11 | 0.716 | 0.4097 | 3.843e-05
626.85 | 0.062 | 1.121 | 0.72 | 0.3868 | 3.981e-05
676.85 | 0.0643 | 1.131 | 0.723 | 0.3666 | 4.113e-05
726.85 | 0.0667 | 1.141 | 0.726 | 0.3482 | 4.244e-05
t | k | Cp | Pr | ragua | m
ºC | W/(m*K) | kJ/(kg*K) | - | kg/m3 | Pa s
Atmospheric air properties as a function of the temperature
Atmospheric air properties as a function
of the temperature
(Table A.4) | [1]

## Water Data (hidden)
0 | 0.569 | 4.217 | 12.99 | 1000 | 0.00175 | 1.75e-06 | 1.3493e-07 | 0.006108
1.85 | 0.574 | 4.211 | 12.22 | 1000 | 0.001652 | 1.652e-06 | 1.3631e-07 | 0.0069793
6.85 | 0.582 | 4.198 | 10.26 | 1000 | 0.001422 | 1.422e-06 | 1.3864e-07 | 0.0099092
11.85 | 0.59 | 4.189 | 8.81 | 1000 | 0.001225 | 1.225e-06 | 1.4085e-07 | 0.013876
16.85 | 0.598 | 4.184 | 7.56 | 999.001 | 0.00108 | 1.0811e-06 | 1.4307e-07 | 0.019178
21.85 | 0.606 | 4.181 | 6.62 | 998.004 | 0.000959 | 9.6092e-07 | 1.4523e-07 | 0.026181
26.85 | 0.613 | 4.179 | 5.83 | 997.009 | 0.000855 | 8.5756e-07 | 1.4713e-07 | 0.035323
31.85 | 0.62 | 4.178 | 5.2 | 995.0249 | 0.000769 | 7.7284e-07 | 1.4914e-07 | 0.047132
36.85 | 0.628 | 4.178 | 4.62 | 993.0487 | 0.000695 | 6.9986e-07 | 1.5136e-07 | 0.062228
41.85 | 0.634 | 4.179 | 4.16 | 991.0803 | 0.000631 | 6.3668e-07 | 1.5308e-07 | 0.081341
46.85 | 0.64 | 4.18 | 3.77 | 989.1197 | 0.000577 | 5.7758e-07 | 1.5326e-07 | 0.10532
51.85 | 0.645 | 4.182 | 3.42 | 987.1668 | 0.000528 | 5.3486e-07 | 1.5624e-07 | 0.13513
56.85 | 0.651 | 4.184 | 3.15 | 984.252 | 0.000489 | 4.9682e-07 | 1.5784e-07 | 0.1719
61.85 | 0.656 | 4.186 | 2.88 | 982.3183 | 0.000453 | 4.6115e-07 | 1.5953e-07 | 0.21689
66.85 | 0.66 | 4.188 | 2.66 | 979.4319 | 0.00042 | 4.2882e-07 | 1.609e-07 | 0.27153
71.85 | 0.664 | 4.191 | 2.45 | 976.5625 | 0.000389 | 3.9834e-07 | 1.6321e-07 | 0.33742
76.85 | 0.668 | 4.195 | 2.29 | 973.7098 | 0.000365 | 3.7485e-07 | 1.6354e-07 | 0.41632
81.85 | 0.671 | 4.199 | 2.14 | 970.8738 | 0.000343 | 3.5329e-07 | 1.6459e-07 | 0.51022
86.85 | 0.674 | 4.203 | 2.02 | 967.118 | 0.000324 | 3.3502e-07 | 1.6581e-07 | 0.62127
91.85 | 0.677 | 4.209 | 1.91 | 963.3911 | 0.000306 | 3.1763e-07 | 1.6696e-07 | 0.75183
96.85 | 0.679 | 4.214 | 1.8 | 960.6148 | 0.000289 | 3.0085e-07 | 1.6774e-07 | 0.90449
100 | 0.68 | 4.217 | 1.76 | 957.8544 | 0.000279 | 2.9128e-07 | 1.6835e-07 | 1.0133
t | k | Cp | Pr | ragua | m | n | a | Psat
ºC | W/(m*K) | kJ/(kg*K) | - | kg/m3 | Pa s | m2/s | m2/s | bar
Saturation properties of water as a function of the temperature
Saturated Water Properties as a Function
of Temperature (Table A.6) |  | [1]

## 6.CS_Imp (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2
3 | Pipe Thickness [mm], according ASME B36.10M
4
5 | [6 empty] | ASME B36.10M SCHEDULE / IDENTIFICATION | [9 empty] | Application |  | Dn = | 24 | mm
6 | Size | dext | 5 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | STD | XS | XXS | (with input validation) |  | SCH = | XS
7 | 0.5 | 21.3 | 1.65 | 2.11 | - | 2.41 | 2.77 | - | 3.73 | - | 0 | - | 4.78 | 2.77 | 3.73 | 7.47 | di = | Pipe_Imp_CS_Dint_dn_sch |  | #NAME? | mm
8 | 0.75 | 26.7 | 1.65 | 2.11 | - | 2.41 | 2.87 | - | 3.91 | - | 0 | - | 5.56 | 2.87 | 3.91 | 7.82 | de = | Pipe_Imp_CS_Dext_dn |  | #NAME? | mm
9 | 1 | 33.4 | 1.65 | 2.77 | - | 2.9 | 3.38 | - | 4.55 | - | 0 | - | 6.35 | 3.38 | 4.55 | 9.09 | s = | Pipe_Imp_CS_Thickness_dn_sch |  | #NAME? | mm
10 | 1.5 | 48.3 | 1.65 | 2.77 | - | 3.18 | 3.68 | - | 5.08 | - | 0 | - | 7.14 | 3.68 | 5.08 | 10.15
11 | 2 | 60.3 | 1.65 | 2.77 | - | 3.18 | 3.91 | - | 5.54 | - | 0 | - | 8.74 | 3.91 | 5.54 | 11.07 | Application |  | Dn = | 16 | mm
12 | 3 | 88.9 | 2.11 | 3.05 | - | 4.78 | 5.49 | - | 7.62 | - | 0 | - | 11.13 | 5.49 | 7.62 | 15.24 | (without input validation) |  | SCH = | 81
13 | 4 | 114.3 | 2.11 | 3.05 | - | 4.78 | 6.02 | - | 8.56 | - | 11.13 | - | 13.49 | 6.02 | 8.56 | 17.12 | di = | Pipe_Imp_CS_Dint_dn_sch |  | #NAME? | mm
14 | 5 | 141.3 | 2.77 | 3.4 | - | - | 6.55 | - | 9.53 | - | 12.7 | - | 15.88 | 6.55 | 9.53 | 19.05 | de = | Pipe_Imp_CS_Dext_dn |  | #NAME? | mm
15 | 6 | 168.3 | 2.77 | 3.4 | - | - | 7.11 | - | 10.97 | - | 14.27 | - | 18.26 | 7.11 | 10.97 | 21.95 | s = | Pipe_Imp_CS_Thickness_dn_sch |  | #NAME? | mm
16 | 8 | 219.1 | 2.77 | 3.76 | 6.35 | 7.04 | 8.18 | 10.31 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01 | 8.18 | 12.7 | 22.23 | The shedule entered is wrong
17 | 10 | 273 | 3.4 | 4.19 | 6.35 | 7.8 | 9.27 | 12.7 | 15.09 | 18.26 | 21.44 | 25.4 | 28.58 | 9.27 | 12.7 | 25.4
18 | 12 | 323.8 | 3.96 | 4.57 | 6.35 | 8.38 | 10.31 | 14.27 | 17.48 | 21.44 | 25.4 | 28.58 | 33.32 | 9.53 | 12.7 | 25.4
19 | 14 | 355.6 | 3.96 | 6.35 | 7.92 | 9.53 | 11.13 | 15.09 | 19.05 | 23.83 | 27.79 | 31.75 | 35.71 | 9.53 | 12.7 | -
20 | 16 | 406.4 | 4.19 | 6.35 | 7.92 | 9.53 | 12.7 | 16.66 | 21.44 | 26.19 | 30.96 | 36.53 | 40.49 | 9.53 | 12.7 | -
21 | 18 | 457 | 4.19 | 6.35 | 7.92 | 11.13 | 14.27 | 19.05 | 23.83 | 29.36 | 34.93 | 39.67 | 45.24 | 9.53 | 12.7 | -
22 | 20 | 508 | 4.78 | 6.35 | 9.53 | 12.7 | 15.09 | 20.62 | 26.19 | 32.54 | 38.1 | 44.45 | 50.01 | 9.53 | 12.7 | -
23 | 22 | 559 | 4.78 | 6.35 | 9.53 | 12.7 | - | 22.23 | 28.58 | 34.93 | 41.28 | 47.63 | 53.98 | 9.53 | 12.7 | -
24 | 24 | 610 | 5.54 | 6.35 | 9.53 | 14.27 | 17.48 | 24.61 | 30.96 | 38.89 | 46.02 | 52.37 | 59.54 | 9.53 | 12.7 | -
25 | 26 | 660 | - | 7.92 | 12.7 | 15.88 | - | - | - | - | - | - | - | 9.53 | 12.7 | -
26 | 28 | 711 | - | 7.92 | 12.7 | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
27 | 30 | 762 | 6.35 | 7.92 | 12.7 | 15.88 | - | - | - | - | - | - | - | 9.53 | 12.7 | -
28 | 32 | 813 | - | 7.92 | 12.7 | 15.88 | 17.48 | - | - | - | - | - | - | 9.53 | 12.7 | -
29 | 34 | 864 | - | 7.92 | 12.7 | 15.88 | 17.48 | - | - | - | - | - | - | 9.53 | 12.7 | -
30 | 36 | 914 | - | 7.92 | 12.7 | 15.88 | 19.05 | - | - | - | - | - | - | 9.53 | 12.7 | -
31 | 38 | 965 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
32 | 40 | 1016 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
33 | 42 | 1067 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
34 | 44 | 1118 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
35 | 46 | 1168 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
36 | 48 | 1219 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
'PipeImp_CS_Dext_dn
'The function PipeImp_CS_Dext_dn gives the exterior diameter of a pipe with
'nominal diameter dn [in]
'If the diameter is a fraction, the input cell has to be formated as a fraction
Function PipeImp_CS_Dext_dn(Dn)
Dim msg As String
Dim C(36, 3) As Variant
Mensaje = "NO"
' Exterior diameters according ASME B36.10M, from Sheet 6.CS_Imp, 3th column
For m = 1 To 36
C(m, 3) = ThisWorkbook.Worksheets("6.CS_Imp").Cells(m, 3).Value
Next m
' The corresponding line of the matrix C is asigned to its Dn-value
If Dn = 0.5 Then
x = 7
ElseIf Dn = 0.75 Then x = 8
ElseIf Dn = 1 Then x = 9
ElseIf Dn = 1.5 Then x = 10
ElseIf Dn = 2 Then x = 11
ElseIf Dn = 3 Then x = 12
ElseIf Dn = 4 Then x = 13
ElseIf Dn = 5 Then x = 14
ElseIf Dn = 6 Then x = 15
ElseIf Dn = 8 Then x = 16
ElseIf Dn = 10 Then x = 17
ElseIf Dn = 12 Then x = 18
ElseIf Dn = 14 Then x = 19
ElseIf Dn = 16 Then x = 20
ElseIf Dn = 18 Then x = 21
ElseIf Dn = 20 Then x = 22
ElseIf Dn = 22 Then x = 23
ElseIf Dn = 24 Then x = 24
ElseIf Dn = 26 Then x = 26
ElseIf Dn = 28 Then x = 26
ElseIf Dn = 30 Then x = 27
ElseIf Dn = 32 Then x = 28
ElseIf Dn = 34 Then x = 29
ElseIf Dn = 36 Then x = 30
ElseIf Dn = 38 Then x = 31
ElseIf Dn = 40 Then x = 32
ElseIf Dn = 42 Then x = 33
ElseIf Dn = 44 Then x = 34
ElseIf Dn = 46 Then x = 35
ElseIf Dn = 48 Then x = 36
' If the Dn-value is not within the given values,
' The function returns Dext = "N/A"
Else
PipeImp_CS_Dext_dn = "N/A"
Exit Function
End If
' In case the input value for Dn was identified and therefore an x-value "x" has been defined,
' the value of the matrix element (x,3) is assigned to de exterior diameter Dext
PipeImp_CS_Dext_dn = C(x, 3)
End Function
'PipeImp_CS_Thickness_dn_sch
'The function PipeImp_CS_Thickness_dn_sch gives the thickness of a pipe with
'nominal diameter dn [in] and schedule sch
'If the diameter is a fraction, the input cell ha to be formated as a fraction
Function PipeImp_CS_Thickness_dn_sch(Dn, SCH)
Dim C(36, 17) As Variant
' Thickness according ASME B36.10M, from Sheet 6.CS_Imp
For m = 1 To 36
For j = 1 To 17
C(m, j) = ThisWorkbook.Worksheets("6.CS_Imp").Cells(m, j).Value
Next j
Next m
If PipeImp_CS_Dext_dn(Dn) = "N/A" Then
PipeImp_CS_Thickness_dn_sch = "N/A"
Exit Function
End If
If Dn = 0.5 Then
x = 7
ElseIf Dn = 0.75 Then x = 8
ElseIf Dn = 1 Then x = 9
ElseIf Dn = 1.5 Then x = 10
ElseIf Dn = 2 Then x = 11
ElseIf Dn = 3 Then x = 12
ElseIf Dn = 4 Then x = 13
ElseIf Dn = 5 Then x = 14
ElseIf Dn = 6 Then x = 15
ElseIf Dn = 8 Then x = 16
ElseIf Dn = 10 Then x = 17
ElseIf Dn = 12 Then x = 18
ElseIf Dn = 14 Then x = 19
ElseIf Dn = 16 Then x = 20
ElseIf Dn = 18 Then x = 21
ElseIf Dn = 20 Then x = 22
ElseIf Dn = 22 Then x = 23
ElseIf Dn = 24 Then x = 24
ElseIf Dn = 26 Then x = 26
ElseIf Dn = 28 Then x = 26
ElseIf Dn = 30 Then x = 27
ElseIf Dn = 32 Then x = 28
ElseIf Dn = 34 Then x = 29
ElseIf Dn = 36 Then x = 30
ElseIf Dn = 38 Then x = 31
ElseIf Dn = 40 Then x = 32
ElseIf Dn = 42 Then x = 33
ElseIf Dn = 44 Then x = 34
ElseIf Dn = 46 Then x = 35
ElseIf Dn = 48 Then x = 36
Else
PipeImp_CS_Thickness_dn_sch(Dn, SCH) = "N/A"
Exit Function
End If
If SCH = 5 Then
Y = 4
ElseIf SCH = 10 Then Y = 5
ElseIf SCH = 20 Then Y = 6
ElseIf SCH = 30 Then Y = 7
ElseIf SCH = 40 Then Y = 8
ElseIf SCH = 60 Then Y = 9
ElseIf SCH = 80 Then Y = 10
ElseIf SCH = 100 Then Y = 11
ElseIf SCH = 120 Then Y = 12
ElseIf SCH = 140 Then Y = 13
ElseIf SCH = 160 Then Y = 14
ElseIf SCH = "STD" Then Y = 15
ElseIf SCH = "XS" Then Y = 16
ElseIf SCH = "XXS" Then Y = 17
Else
PipeImp_CS_Thickness_dn_sch = "N/A"
Exit Function
End If
PipeImp_CS_Thickness_dn_sch = C(x, Y)
If PipeImp_CS_Thickness_dn_sch = " - " Then
PipeImp_CS_Thickness_dn_sch = "N/A"
End If
End Function
'PipeImp_CS_Dint_dn_sch
'The function PipeImp_CS_Dint_dn_sch gives the interior diameter of a pipe with
'nominal diameter dn [in] and schedule sch
'If the diameter is a fraction, the input cell ha to be formated as a fraction
Function PipeImp_CS_Dint_dn_sch(Dn, SCH)
If PipeImp_CS_Thickness_dn_sch(Dn, SCH) = "N/A" Then
PipeImp_CS_Dint_dn_sch = "N/A"
Exit Function
End If
If PipeImp_CS_Dext_dn(Dn) = "N/A" Then
PipeImp_CS_Dint_dn_sch = "N/A"
Exit Function
End If
PipeImp_CS_Dint_dn_sch = PipeImp_CS_Dext_dn(Dn) - PipeImp_CS_Thickness_dn_sch(Dn, SCH) * 2
End Function

## 1.- Venting diameter
Tank venting diameter according API 2000
cjc. Rev. 10.08.2016
Operating conditions |  |  | Auxiliary variables |  |  | Air temperature |  |  | Venting area. Eq. 1
Water flow entering the tank |  |  | Evacuation flow (API 2000) |  |  | t = | 10 | °C | Q = | 404 | Nm3/h
Q = | 200 | m3/h | See sheet. "2 -Venting flow" |  |  | T = | 283.15 | K | Pin = | 0.906 | bar
Local temperature and heigth above sea level |  |  | In the case of water, select | [5 empty] | M = | 28.966 | kg/kmol
tamb = | 10 | °C | the case of boiling lower |  |  | Outside pressure |  |  | T = | 283.15 | K
H = | 2637.6 | m.a.s.l. | than 149 ° C. |  |  | Pamb = | 73.4003 | kPa | Z = | 0.99973 | -
Allowable overpressure in tank |  |  | For a movement of fluid into the |  |  | Pout = | Pamb | Pa | k = | 1.4 | -
DP = | 17.2 | kPa (*) | tank (air leaving the tank), the |  |  | Pout = | 73.4003 | kPa | Pout = | 0.734 | bar | Fig. Venting in roof tank
|  |  | venting requirement ratio is |  |  | Pout = | 0.734 | bar | A = | 8.3039 | cm²
Air properties |  |  | Vn_unit = | 2.02
Local atmospheric pressure | [5 empty] | Inside pressure
p = | 101,325* (1 -2,25577E-5 * H)^5,25588 |  | (from sheet 2.- Venting flow) |  |  | Pin = | Pout + DP |  | Calculated diameter
H = | 2637.6 | m.a.s.l. |  |  |  | Pout = | 73.4003 | kPa | d = | 2 * (A / (p) )^0.5
p = | 73.4003 | kPa | For a water flow entering the tank |  |  | DP = | 17.2 | kPa | A = | 8.3039 | cm²
Ratio of specific weights |  |  | Q = | 200 | m3/h | Pin = | 90.6003 | kPa | d = | 3.2516 | cm | Eq. 1
k = | 1.4 |  | The required venting is |  |  | Pin = | 0.906 | bar (abs) | d = | 32.5159 | mm
(the value of "k" is practically constant |  |  | Vn = | Vn_unit * Q |  |  |  |  | d = | 1.2802 | in
in a wide range) |  |  | Vn_unit = | 2.02
Air molar mass |  |  | Q = | 200 | m3/h |  |  |  | Selected diameter
M = | 28.966 | kg/kmol | Vn = | 404 | Nm3/h |  |  |  | Sea d = | 4 | in
Compression factor
Z = | 0.99973 | - | Eq. 1
(this value is practically constant in |  |  | Venting area is determined by equation of API 2000 [1] | [8 empty] | (*) tank overpressure
the normaly used range) |  |  | A = | Q / (12503*Pin * ( (1/(M*T*Z)*(k/(k-1))) * ( (Pout/Pin )^(2/k) - (Pout/Pin )^((k+1)/k) ) )^0.5 ) | [7 empty] | 17.2 kPag = 2.5 psig
Q
d
Pamb
Pin t
(Nm3_air/h)/(m3_liq/h)

## 2.- Venting flow
cjc. Rev. 10.08.2016
API 2000
Venting flow
For the case of water, select the case of
a boiling point lower than 149 °C.
For a movement of fluid into the tank
(air leaving the tank), the venting
requirement is obtained from Table 1B
Vn/Q = | 2.02 | Nm3/h air / m3/h liquid
For a water flow entering the tank
Q = | 200 | m3/h |  | Normal venting requirement
The venting requirement is |  |  |  | Vn/Q = | 2.02 | Nm3/h air / m3/h liquid
Vn = | (Vn/Q) *Q
Vn/Q = | 2.02
Q = | 200 | m3/h
Vn = | 404 | Nm3/h

## 4.- API (SI)
cjc. Rev. 10.08.2016
|  | Q = | 404 | Nm3/h
|  | Pin = | 0.906 | bar
|  | k = | 1.4 | -
|  | M = | 28.966 | kg/kmol
|  | T = | 283.15 | K
|  | Z = | 0.99973 | -
|  | Pout = | 0.734 | bar
|  | A = | 8.3039 | cm²
A = | Q / (12503*Pin * ( (1/(M*T*Z)*(k/(k-1))) * ( (Pout/Pin )^(2/k) - (Pout/Pin )^((k+1)/k) ) )^0.5 ) |  |  |  | (4B)

## 5.- API ( Imp)
cjc. Rev. 10.08.2016
[6 empty] | Normal to real flow |  |  | Real volumetric flow rate
[6 empty] | Flujo volumétrico normal |  |  | V = | (Pn/Pop) * (Top/Tn) * Vn
[6 empty] | Vn = | 1 | Nm3 | Pn = | 101325 | Pa
[9 empty] | Tn = | 273.15 | K
[6 empty] | Normal conditions |  |  | Pop = | 90600.3373 | Pa (abs)
[6 empty] | Pn = | 101325 | Pa | Top = | 288.7056 | °C
[6 empty] | Tn = | 273.15 | K | Vn = | 1 | Nm3
[9 empty] | V = | 1.1821 | m3
[6 empty] | Local atmospheric presure |  |  | V = | 41.7387 | scf
[6 empty] | Patm_loc = | 101.325 | kPa
A = Q / (278700*Pin * ( (1/(M*T*Z)*(k/(k-1))) * ( (Pout/Pin )^(2/k) - (Pout/Pin )^((k+1)/k) ) )^0.5 ) | [5 empty] | Operation conditions
[6 empty] | Pop = | 17.2 | kPa g
Q = | 404 | Nm3/h | Q = | 16862.4167 | SCF | top = | 60 | °F
Pin = | 0.906 | bar (abs) | Pin = | 13.1405 | psia | top = | 15.5556 | °C
k = | 1.4 | - | k = | 1.4
M = | 28.966 | kg/kmol | M = | 28.966 |  | Operation absolute pressure
T = | 283.15 | K | T = | 509.67 | R | Pop = | Patm_loc + Pop |  | 1 m3 = | 35.31 | cf
Z = | 0.99973 | - | Z = | 0.99973 |  | Patm_loc = | 101.325 | kPa | 1 Nm³ = | 41.7387 | scf
Pout = | 0.734 | bar | Pout = | 10.6458 |  | Pop = | 17.2 | kPa g | 1 bar = | 14.5038 | psi
|  |  | A = | 1.4383 | in² | Pop = | 118.525 | kPa | 1 in² = | 6.4516 | cm²
|  |  | A = | 9.2794 | cm² | Pop = | 118525 | Pa
Operation temperature
[6 empty] | Top = | 288.7056 | K

## 6.- Air compressibility
Compressibility factor for air (experimental values)
Pressure, bar (absolute)
Temp, K | 1 | 5 | 10 | 20 | 40 | 60 | 80 | 100 | 150 | 200 | 250 | 300 | 400 | 500
75 | 0.0052 | 0.026 | 0.0519 | 0.1036 | 0.2063 | 0.3082 | 0.4094 | 0.5099 | 0.7581 | 1.0125
80 |  | 0.025 | 0.0499 | 0.0995 | 0.1981 | 0.2958 | 0.3927 | 0.4887 | 0.7258 | 0.9588 | 1.1931 | 1.4139
90 | 0.9764 | 0.0236 | 0.0453 | 0.094 | 0.1866 | 0.2781 | 0.3686 | 0.4681 | 0.6779 | 0.8929 | 1.1098 | 1.311 | 1.7161 | 2.1105
100 | 0.9797 | 0.8872 | 0.0453 | 0.09 | 0.1782 | 0.2635 | 0.3498 | 0.4337 | 0.6386 | 0.8377 | 1.0395 | 1.2227 | 1.5937 | 1.9536
120 | 0.988 | 0.9373 | 0.886 | 0.673 | 0.1778 | 0.2557 | 0.3371 | 0.4132 | 0.5964 | 0.772 | 0.953 | 1.1076 | 1.5091 | 1.7366
140 | 0.9927 | 0.9614 | 0.9205 | 0.8297 | 0.5856 | 0.3313 | 0.3737 | 0.434 | 0.5909 | 0.7699 | 0.9114 | 1.0393 | 1.3202 | 1.5903
160 | 0.9951 | 0.9748 | 0.9489 | 0.8954 | 0.7803 | 0.6603 | 0.5696 | 0.5489 | 0.634 | 0.7564 | 0.884 | 1.0105 | 1.2585 | 1.497
180 | 0.9967 | 0.9832 | 0.966 | 0.9314 | 0.8625 | 0.7977 | 0.7432 | 0.7084 | 0.718 | 0.7986 | 0.9 | 1.0068 | 1.2232 | 1.4361
200 | 0.9978 | 0.9886 | 0.9767 | 0.9539 | 0.91 | 0.8701 | 0.8374 | 0.8142 | 0.8061 | 0.8549 | 0.9311 | 1.0185 | 1.2054 | 1.3944
250 | 0.9992 | 0.9957 | 0.9911 | 0.9822 | 0.9671 | 0.9549 | 0.9463 | 0.9411 | 0.945 | 0.9713 | 1.0152 | 1.0702 | 1.199 | 1.3392
283 | 0.99966 | 0.99768 | 0.99526 | 0.99065 | 0.98334 | 0.97813 | 0.97534 | 0.97535 | 0.98618 | 1.0118 | 1.0493 | 1.0957 | 1.2045 | 1.3241
300 | 0.9999 | 0.9987 | 0.9974 | 0.995 | 0.9917 | 0.9901 | 0.9903 | 0.993 | 1.0074 | 1.0326 | 1.0669 | 1.1089 | 1.2073 | 1.3163
350 | 1 | 1.0002 | 1.0004 | 1.0014 | 1.0038 | 1.0075 | 1.0121 | 1.0183 | 1.0377 | 1.0635 | 1.0947 | 1.1303 | 1.2116 | 1.3015
400 | 1.0002 | 1.0012 | 1.0025 | 1.0046 | 1.01 | 1.0159 | 1.0229 | 1.0312 | 1.0533 | 1.0795 | 1.1087 | 1.1411 | 1.2117 | 1.289
450 | 1.0003 | 1.0016 | 1.0034 | 1.0063 | 1.0133 | 1.021 | 1.0287 | 1.0374 | 1.0614 | 1.0913 | 1.1183 | 1.1463 | 1.209 | 1.2778
500 | 1.0003 | 1.002 | 1.0034 | 1.0074 | 1.0151 | 1.0234 | 1.0323 | 1.041 | 1.065 | 1.0913 | 1.1183 | 1.1463 | 1.2051 | 1.2667
600 | 1.0004 | 1.0022 | 1.0039 | 1.0081 | 1.0164 | 1.0253 | 1.034 | 1.0434 | 1.0678 | 1.092 | 1.1172 | 1.1427 | 1.1947 | 1.2475
800 | 1.0004 | 1.002 | 1.0038 | 1.0077 | 1.0157 | 1.024 | 1.0321 | 1.0408 | 1.0621 | 1.0844 | 1.1061 | 1.1283 | 1.172 | 1.215
1000 | 1.0004 | 1.0018 | 1.0037 | 1.0068 | 1.0142 | 1.0215 | 1.029 | 1.0365 | 1.0556 | 1.0744 | 1.0948 | 1.1131 | 1.1515 | 1.1889

## 8.- Bernoulli
Bernoulli Equation | http://www.engineeringtoolbox.com/bernouilli-equation-d_183.html
Conservation of energy - non-viscous, incompressible fluid in steady flow
A statement of the conservation of energy in a form useful for solving problems involving fluids. For a non-viscous, incompressible fluid in steady flow, the sum of pressure, potential and kinetic energies per unit volume is constant at any point
A special form of the Euler’s equation derived along a fluid flow streamline is often called the Bernoulli Equation
For steady state incompressible flow the Euler equation becomes (1). If we integrate (1) along the streamline it becomes (2). (2) can further be modified to (3) by dividing by gravity.
Head of Flow
Equation (3) is often referred to the head because all elements has the unit of length.
Dynamic Pressure
(2) and (3) are two forms of the Bernoulli Equation for steady state incompressible flow. If we assume that the gravitational body force is negligible, (3) can be written as (4). Both elements in the equation have the unit of pressure and it's common to refer the flow velocity component as the dynamic pressure of the fluid flow (5).
Since energy is conserved along the streamline, (4) can be expressed as (6). Using the equation we see that increasing the velocity of the flow will reduce the pressure, decreasing the velocity will increase the pressure.
This phenomena can be observed in a venturi meter where the pressure is reduced in the constriction area and regained after. It can also be observed in a pitot tube where the stagnation pressure is measured. The stagnation pressure is where the velocity component is zero.
Example - Bernoulli Equation and Flow from a Tank through a small Orifice
Liquid flows from a tank through a orifice close to the bottom. The Bernoulli equation can be adapted to a streamline from the surface (1) to the orifice (2) as (e1):
Since (1) and (2)'s heights from a common reference is related as (e2), and the equation of continuity can be expressed as (e3), it's possible to transform (e1) to (e4).
Vented tank
A special case of interest for equation (e4) is when the orifice area is much lesser than the surface area and when the pressure inside and outside the tank is the same - when the tank has an open surface or "vented" to the atmosphere. At this situation the (e4) can be transformed to (e5).
"The velocity out from the tank is equal to speed of a freely body falling the distance h." - also known as Torricelli's Theorem.
Example - outlet velocity from a vented tank
The outlet velocity of a tank with height 10 m can be calculated as
V2 = (2 (9.81 m/s2) (10 m))1/2
= 14 m/s
Pressurized Tank
If the tanks is pressurized so that product of gravity and height (g h) is much lesser than the pressure difference divided by the density, (e4) can be transformed to (e6).
The velocity out from the tank depends mostly on the pressure difference.
Example - outlet velocity from a pressurized tank
The outlet velocity of a pressurized tank where
p1 = 0.2 MN/m2
p2 = 0.1 MN/m2
A2/A1 = 0.01
h = 10 m
can be calculated as
V2 = ( (2/(1-(0.01)2) ((0.2 106 N/m2) - (0.1 106 N/m2))/(1000 kg/m3) + (9.81 m/s2)(10 m)))1/2
= 19.9 m/s
Coefficient of Discharge - Friction Coefficient
Due to friction the real velocity will be somewhat lower than this theoretic examples. If we introduce a friction coefficient c (coefficient of discharge), (e5) can be expressed as (e5b).
The coefficient of discharge can be determined experimentally. For a sharp edged opening it may bee as low as 0.6. For smooth orifices it may bee between 0.95 and 1.

## 9.- Q normal to real
cjc. Rev. 10.08.2016
Flujo real a normal |  |  | Normal volumetric flow rate |  |  | Normal to real flow |  |  | Real volumetric flow rate
Real flow rate data |  |  | Vn = | (Pop/Pn) * (Tn/Top) * V |  | Flujo volumétrico normal |  |  | V = | (Pn/Pop) * (Top/Tn) * Vn
V = | 262 | m3/h | Pop = | 90600.3373 | Pa | Vn = | 404 | Nm3/h | Pn = | 101325 | Pa
t = | 10 | °C | Pn = | 101325 | Pa |  |  |  | Tn = | 273.15 | K
P = | 17.2 | kPa(g) | Tn = | 273.15 | K | Normal conditions |  |  | Pop = | 90600 | Pa
|  |  | Top = | 283.15 | °C | Pn = | 101325 | Pa | Top = | 283.15 | °C
Normal conditions |  |  | V = | 262 | m3/h | Tn = | 273.15 | K | Vn = | 404 | Nm3/h
Pn = | 101325 | Pa | Vn = | 225.9952 | Nm3/h |  |  |  | V = | 468.3658 | m3/h
Tn = | 273.15 | K |  |  |  | Local atmospheric presure
[6 empty] | Patm_loc = | 73.4 | kPa
Local atmospheric presure
Patm_loc = | 73.4003 | kPa |  |  |  | Operation conditions
[6 empty] | Pop = | 17.2 | kPa g
Operation absolute pressure | [5 empty] | top = | 10 | °C
Pop = | Patm_loc + Pop
Patm_loc = | 73.4003 | kPa |  |  |  | Operation absolute pressure
Pop = | 17.2 | kPa g |  |  |  | Pop = | Patm_loc + Pop
Pop = | 90.6003 | kPa |  |  |  | Patm_loc = | 73.4 | kPa
Pop = | 90600.3373 | Pa |  |  |  | Pop = | 17.2 | kPa g
[6 empty] | Pop = | 90.6 | kPa
Operation temperature | [5 empty] | Pop = | 90600 | Pa
Top = | 283.15 | K
Operation temperature
[6 empty] | Top = | 283.15 | K

## Ref
[1]

## Pending (hidden)
Derivación de la ecuación. | Pending