## 1.CS
6	10,3	1,73	2,41	-	-	-	-	1,73	-	2,41	-	-	-	-
8	13,7	2,24	3,02	-	-	-	-	2,24	-	3,02	-	-	-	-		Application			Dn =	8	mm
10	17,1	2,31	3,2	-	-	-	-	2,31	-	3,2	-	-	-	-		(with input validation)			SCH =	40
15	21,3	2,77	3,73	7,47	-	-	-	2,77	-	3,73	-	-	-	4,78		di =	Pipe_CS_Dint_dn_sch =			9,22	mm
20	26,7	2,87	3,91	7,82	-	-	-	2,87	-	3,91	-	-	-	5,56		de =	Pipe_CS_Dext_dn =			13,7	mm
25	33,4	3,38	4,55	9,09	-	-	-	3,38	-	4,55	-	-	-	6,35		s =	Pipe_CS_Thickness_dn_sch =			2,24	mm
32	42,2	3,56	4,85	9,7	-	-	-	3,56	-	4,85	-	-	-	6,35
40	48,3	3,68	5,08	10,15	-	-	-	3,68	-	5,08	-	-	-	7,14
50	60,3	3,91	5,54	11,07	-	-	-	3,91	-	5,54	-	-	-	8,74
65	73	5,16	7,01	14,02	-	-	-	5,16	-	7,01	-	-	-	9,53		Application			Dn =	350	mm
80	88,9	5,49	7,62	15,24	-	-	-	5,49	-	7,62	-	-	-	11,13		(without input validation)			SCH =	40
90	101,6	5,74	8,08	-	-	-	-	5,74	-	8,08	-	-	-	-		di =	Pipe_CS_Dint_dn_sch =			333,34	mm
100	114,3	6,02	8,56	17,12	-	-	-	6,02	-	8,56	-	11,13	-	13,49		de =	Pipe_CS_Dext_dn =			355,6	mm
125	141,3	6,55	9,53	19,05	-	-	-	6,55	-	9,53	-	12,7	-	15,88		s =	Pipe_CS_Thickness_dn_sch =			11,13	mm
150	168,3	7,11	10,97	21,95	-	-	-	7,11	-	10,97	-	14,27	-	18,26		The shedule entered is wrong
200	219,1	8,18	12,7	22,23	-	6,35	7,04	8,18	10,31	12,7	15,09	18,26	20,62	23,01
250	273,1	9,27	12,7	25,4	-	6,35	7,8	9,27	12,7	15,09	18,26	21,44	25,4	28,58
300	323,9	9,53	12,7	25,4	-	6,35	8,38	10,31	14,27	17,48	21,44	25,4	28,58	33,32
350	355,6	9,53	12,7	-	6,35	7,92	9,53	11,13	15,09	19,05	23,83	27,79	31,75	35,71
400	406,4	9,53	12,7	-	6,35	7,92	9,53	12,7	16,66	21,44	26,19	30,96	36,53	40,49
450	457	9,53	12,7	-	6,35	7,92	11,13	14,27	19,05	23,83	29,36	34,93	39,67	45,24
500	508	9,53	12,7	-	6,35	9,53	12,7	15,09	20,62	26,19	32,54	38,1	44,45	50,01
550	559	9,53	12,7	-	6,35	9,53	12,7	-	22,23	28,58	34,93	41,28	47,63	53,98
600	610	9,53	12,7	-	6,35	9,53	14,27	17,48	24,61	30,96	38,89	46,02	52,37	59,54
650	660	9,53	12,7	-	7,92	12,7	-	-	-	-	-	-	-	-
700	711	9,53	12,7	-	7,92	12,7	15,88	-	-	-	-	-	-	-
750	762	9,53	12,7	-	7,92	12,7	15,88	-	-	-	-	-	-	-
800	813	9,53	12,7	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-
850	864	9,53	12,7	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-
900	914	9,53	12,7	-	7,92	12,7	15,88	19,05	-	-	-	-	-	-
1050	1067	9,53	12,7	-	-	-	-	-	-	-	-	-
		STD	ExStr	XxStr	10	20	30	40	60	80	100	120	140	160

AC
6	STD
8	ExStr
10	XxStr
15	10
20	20
25	30
32	40
40	60
50	80
65	100
80	120
90	140
100	160
125
150
200
250
300
350
400
450
500
550
600
650
700
750
800
850
900
1050

## 2.SS
6	10,29	-	1,24	1,73	2,41
8	13,72	-	1,65	2,24	3,02		Application			Dn =	350	mm
10	17,15	-	1,65	2,31	3,2		(with input validation)			SCH =	10S
15	21,34	1,65	2,11	2,77	3,73		di =	Pipe_SS_Dint_dn_sch =			346,04	mm
20	26,67	1,65	2,11	2,87	3,91		de =	Pipe_SS_Dext_dn =			355,6	mm
25	33,4	1,65	2,77	3,38	4,55		s =	Pipe_SS_Thickness_dn_sch =			4,78	mm
32	42,16	1,65	2,77	3,56	4,85
40	48,26	1,65	2,77	3,68	5,08			Pipe_SS_Dext_dn			355,6
50	60,33	1,65	2,77	3,91	5,54
65	73,03	2,11	3,05	5,16	7,01		Application			Dn =	350	mm
80	88,9	2,11	3,05	5,49	7,62		(without input validation)			SCH =	10S
100	114,3	2,11	3,05	6,02	8,56		di =	Pipe_SS_Dint_dn_sch =			346,04	mm
125	141,3	2,77	3,4	6,55	9,52		de =	Pipe_SS_Dext_dn =			355,6	mm
150	168,28	2,77	3,4	7,11	10,97		s =	Pipe_SS_Thickness_dn_sch =			4,78	mm
200	219,08	2,77	3,76	8,18	12,7		The shedule entered is wrong
250	273,05	3,4	4,19	9,27	12,7
300	323,85	3,96	4,57	9,52	12,7
350	355,6	3,96	4,78	-	-
400	406,4	4,19	4,78	-	-
450	457,2	4,19	4,78	-	-
500	508	4,78	5,54	-	-
600	609,6	5,54	6,35	-	-
750	762	6,35	7,92	-	-
NOMINAL / SIZE (DN)	OUTSIDE / DIAM.	5S	10S	40S	80S
		WALL THICKNESS (mm)
STAINLESS STEEL PIPES TO AMERICAN STANDARD ASME B36.19					From Onesteel

2.- Stainless steel pipes
dn	Sch
mm	-
6	5S
8	10S
10	40S
15	80S
20
25
32
40
50
65
80
100
125
150
200
250
300
350
400
450
500
600
750

## 3.PVC
15	-	-	-	-	-	1,5	1,8
20	26,75	-	-	-	1,5	1,9	2,2		Application			Dn =	40	mm
25	33,55	-	-	1,5	1,9	2,3	2,7		(with input validation)			PN =	12
32	42,25	-	-	1,9	2,4	2,9	3,4		di =	Pipe_PVC_Dint_dn_PN			42,85	mm
40	48,25	-	1,5	2,1	2,7	3,3	3,9		de =	Pipe_PVC_Dext_dn			48,25	mm
50	60,35	-	1,8	2,6	3,3	4,1	4,9		s =	Pipe_PVC_Thickness_dn_PN			2,7	mm
65	75,35	1,7	2,2	3,2	4,2	5,1	6,1
80	88,9	2	2,6	3,8	4,9	6,1	7,1
100	114,3	2,5	3,2	4,8	6,3	7,7	9,1
125	140,2	3	4	5,9	7,6	-	-		Application			Dn =	40	mm
150	160,3	3,4	4,5	6,7	8,8	10,8	12,8		(without input validation)			PN =	PN12
200	225,3	-	5,7	8,4	11,1	13,6	16,2		di =	Pipe_PVC_Dint_dn_PN			N/A	mm
225	250,4	4,8	6,3	9,3	12,3	15,2	18		de =	Pipe_PVC_Dext_dn			48,25	mm
250	280,4	-	7,1	10,5	13,7	17	20,1		s =	Pipe_PVC_Thickness_dn_PN			N/A	mm
300	315,5	6	8	11,7	15,5	19,1	22,6		The nominal diameter entered is wrong
375	400,5	7,7	10,1	14,9	19,6	-	-

Standard uPVC Pipe Sizes			From iPlex
NOMINAL / SIZE (DN)	OUTSIDE / DIAM.	4,5	6	9	12	15	18
		WALL THICKNESS (mm)

3.- PVC pipes

## 4.HDPE_PE100
16					2,3
20					2,3		Application			Dn =	355	mm
25					2,3	2,8		(with input validation)			PN =	10
32					2,4	3	3,6		di =	Pipe_HDPE_PE100_Dint_Dn_PN(N2; N3)			312,8	mm
40				2,4	3	3,7	4,5		de =	Pipe_HDPE_PE100_Dext_Dn(N2)			355	mm
50			2,4	3	3,7	4,6	5,6		s =	Pipe_HDPE_PE100_Thickness_Dn_PN(N2; N3)			21,1	mm
63		2,3	3	3,8	4,7	5,8	7,1
75		2,8	3,6	4,5	5,6	6,8	8,4
90	2,3	3,3	4,3	5,4	6,7	8,2	10,1
110	2,7	4	5,3	6,6	8,1	10	12,3		Application			Dn =	355	mm
125	3,1	4,6	6	7,4	9,2	11,4	14		(without input validation)			PN =	10
140	3,5	5,1	6,7	8,3	10,3	12,7	15,7		di =	Pipe_HDPE_PE100_Dint_Dn_PN(N2; N3)			312,8	mm
160	4	5,8	7,7	9,5	11,8	14,6	17,9		de =	Pipe_HDPE_PE100_Dext_Dn(N2)			355	mm
180	4,4	6,6	8,6	10,7	13,3	16,4	20,1		s =	Pipe_HDPE_PE100_Thickness_Dn_PN(N2; N3)			21,1	mm
200	4,9	7,3	9,6	11,9	14,7	18,2	22,4		The nominal pressure entered is wrong
225	5,5	8,2	10,8	13,4	16,6	20,5	25,2
250	6,2	9,1	11,9	14,8	18,4	22,7	27,9
280	6,9	10,2	13,4	16,6	20,6	25,4	31,3
315	7,7	11,4	15	18,7	23,2	28,6	35,2
355	8,7	12,9	16,9	21,1	26,1	32,2	39,7
400	9,8	14,5	19,1	23,7	29,4	36,3	44,7
450	11	16,3	21,5	26,7	33,1	40,9	50,3
500	12,3	18,1	23,9	29,7	36,8	45,4	55,8
560	13,7	20,3	26,7	33,2	41,2	50,8
630	15,4	22,8	30	37,4	46,2	57,2
710	17,4	25,7	33,9	42,1	52,2
800	19,6	29	38,1	47,4	58,8
900	22	32,6	42,6	53,3
1000	24,5	36,2	47,7	59,3
1200	29,4	43,4	57,2
1400	34,3	50,6
1600	39,2	57,9
Dn [mm]	4	6	8	10	12,5	16	20
	Presiones nominales PN [bar]
HDPE PE100

dn	PN
mm	bar
16	4
20	6
25	8
32	10
40	12,5
50	16
63	20
75
90
110
125
140
160
180
200
225
250
280
315
355
400
450
500
560
630
710
800
900
1000
1200
1400
1600

	http://www.vinilit.cl/pdf_2/tub_fittings_hdpe_min.pdf					http://www.vinilit.cl/pdf_2/tub_fittings_hdpe_min.pdf

## 4.HDPE_PE80
16					2,2	1
20					1,9	2,8	2		Application			Dn =	355	mm
25					2,3	3,5	3		(with input validation)			PN =	10
32				1,8	2,9	4,4	4		di =	Pipe_HDPE_PE80_Dint_Dn_PN(N2,N3)			290,6	mm
40			1,8	2,3	3,7	5,5	5		de =	Pipe_HDPE_PE80_Dext_Dn(N2)			355	mm
50		1,8	2,0	2,9	4,6	6,9	6		s =	Pipe_HDPE_PE80_Thickness_Dn_PN(N2,N3)			32,2	mm
63	1,8	2,0	2,5	3,6	5,8	8,6	7
75	1,9	2,3	2,9	4,3	6,8	10,3	8
90	2,2	2,8	3,5	5,1	8,2	12,3	9
110	2,7	3,4	4,2	6,3	10,0	15,1	10		Application			Dn =	355	mm
125	3,1	3,9	4,8	7,1	11,4	17,1	11		(without input validation)			PN =	11
140	3,5	4,3	5,4	8,0	12,7	19,2	12		di =	Pipe_HDPE_PE80_Dint_Dn_PN			N/A	mm
160	4,0	4,9	6,2	9,1	14,6	21,9	13		de =	Pipe_CS_Dext_dn			355	mm
180	4,4	5,5	6,9	10,2	16,4	24,6	14		s =	Pipe_HDPE_PE100_Thickness_Dn_PN			N/A	mm
200	4,9	6,2	7,7	11,4	18,2	27,4	15		The nominal pressure entered is wrong
225	5,5	6,9	8,6	12,8	20,5	30,8	16
250	6,2	7,7	9,6	14,2	22,7	34,2	17
280	6,9	8,6	10,7	15,9	25,4	38,3	18		Application with imput diameter in imperial units
315	7,7	9,7	12,1	17,9	28,6	43,1	19
355	8,7	10,9	13,6	20,1	32,2	48,5	20		Application			Dn =	14	in
400	9,8	12,3	15,3	22,7	36,3	54,7	21		(without input validation)			PN =	10
450	11,0	13,8	17,2	25,5	40,9	61,5	22		di =	Pipe_Imp_HDPE_PE80_Dint_Dn_PN(N2,N3)			290,6	mm
500	12,3	15,3	19,1	28,4	45,4	68,3	23		de =	Pipe_Imp_HDPE_PE80_Dext_Dn(N2)			355	mm
560	13,7	17,2	21,4	31,7	50,8		24		s =	Pipe_Imp_HDPE_PE80_Thickness_Dn_PN(N2,N3)			32,2	mm
630	15,4	19,3	24,1	35,7	57,2		25
710	17,4	21,8	27,2	40,2	64,5		26
800	19,6	24,5	30,6	45,3			27
900	22,0	27,6	34,4	51,0			28
1000	24,5	30,6	38,2	56,7			29
1100	26,9	33,7	42,0	62,4			30
1200	29,4	36,7	45,9	68,0			31
1400	34,4	42,9	53,5				32
1600	39,2	49,0	61,2				33
Dn [mm]	2 1/2	3,2	4	6	10	16
	Presiones nominales PN [bar]
	HDPE PE80 DIN 8074 / ISO 4427
Espesor [mm]
1	2	3	4	5	6	7

HDPE 80 DIN 8074
dn	PN
mm	bar
16	2,5
20	3,2
25	4
32	6
40	10
50	16
63
75
90
110
125
140
160
180
200
225
250
280
315
355
400
450
500
560
630
710
800
900
1000
1100
1200
1400
1600

## 5.FRP
Standard FRP Pipe Sizes (Hobas)
		WALL THICKNESS (mm)
dn [mm]	de [mm]	Class4 SN5k	Class6 SN5k	Class6 SN10k	Class10 SN5k	Class10 SN10k	Class12.5 SN5k	Class12.5 SN10k	Class16 SN10k	Class20 SN10k	Class25 SN10k
300	345	7	7	10	7	8	7	8	8	8	8		Application			Dn =	525	mm
375	426	8	8	11	8	10	8	10	10	10	10		(with input validation)			PN =	Class20 SN10k
450	507	10	10	13	9	12	9	11	11	11	11		di =	Pipe_FRP_Dint_dn_sch =			561	mm
525	587	11	11	15	11	13	11	13	13	13	13		de =	Pipe_FRP_Dext_dn =			587	mm
600	667	13	12	17	12	15	12	15	14	14	-		s =	Pipe_FRP_Thickness_dn_sch =			13	mm
675	747	14	14	19	13	17	13	16	16	-	-
750	826	15	15	20	14	18	15	18	17	-	-
900	924	17	17	23	16	20	16	20	19	-	-
1000	1026	19	18	25	18	22	17	22	21	-	-		Application			Dn =	750	mm
1200	1229	22	22	30	21	26	21	26	25	-	-		(without input validation)			PN =	Class6 SN10 k
					di =	Pipe_FRP_Dint_dn_sch =			N/A	mm
					de =	Pipe_FRP_Dext_dn =			826	mm
			From iPlex					s =	Pipe_FRP_Thickness_dn_sch =			N/A	mm
NOMINAL / SIZE (DN)	OUTSIDE / DIAM.					The nominal pressure entered is wrong

5.- FRP pipes

FRP
dn	PN
mm	bar
300	Class4 SN5k
375	Class6 SN5k
450	Class6 SN10k
525	Class10 SN5k
600	Class10 SN10k
675	Class12.5 SN5k
750	Class12.5 SN10k
900	Class16 SN10k
1000	Class20 SN10k
1200	Class25 SN10k

## 6.CS_Imp
1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17
2
3	Pipe Thickness [mm], according ASME B36.10M
4
5							ASME B36.10M SCHEDULE / IDENTIFICATION											Application			Dn =	10	in
6	Size	dext	5	10	20	30	40	60	80	100	120	140	160	STD	XS	XXS		(with input validation)			SCH =	XXS	-
7	1/2	21,3	1,65	2,11	-	2,41	2,77	-	3,73	-	0	-	4,78	2,77	3,73	7,47		di =	Pipe_Imp_CS_Dint_dn_sch			N/A	mm
8	3/4	26,7	1,65	2,11	-	2,41	2,87	-	3,91	-	0	-	5,56	2,87	3,91	7,82		de =	Pipe_Imp_CS_Dext_dn			406,4	mm
9	1	33,4	1,65	2,77	-	2,9	3,38	-	4,55	-	0	-	6,35	3,38	4,55	9,09		s =	Pipe_Imp_CS_Thickness_dn_sch			N/A	mm
10	1 1/4	42,2	1,65	2,77		2,97	3,56		4,85				6,35	3,56	4,85	9,7
11	1 1/2	48,3	1,65	2,77	-	3,18	3,68	-	5,08	-	0	-	7,14	3,68	5,08	10,15
12	2	60,3	1,65	2,77	-	3,18	3,91	-	5,54	-	0	-	8,74	3,91	5,54	11,07		Application			Dn =	16	in
13	2 1/2	73	2,11	3,05		4,78	5,16		7,01				9,53	5,16	7,01	14,02
14	3	88,9	2,11	3,05	-	4,78	5,49	-	7,62	-	0	-	11,13	5,49	7,62	15,24		(without input validation)			SCH =	81
15	3 1/2	101,6	2,11	3,05		4,78	5,74		8,08					5,74	8,08
16	4	114,3	2,11	3,05	-	4,78	6,02	-	8,56	-	11,13	-	13,49	6,02	8,56	17,12		di =	Pipe_Imp_CS_Dint_dn_sch			N/A	mm
17	5	141,3	2,77	3,4	-	-	6,55	-	9,53	-	12,7	-	15,88	6,55	9,53	19,05		de =	Pipe_Imp_CS_Dext_dn			559	mm
18	6	168,3	2,77	3,4	-	-	7,11	-	10,97	-	14,27	-	18,26	7,11	10,97	21,95		s =	Pipe_Imp_CS_Thickness_dn_sch			N/A	mm
19	8	219,1	2,77	3,76	6,35	7,04	8,18	10,31	12,7	15,09	18,26	20,62	23,01	8,18	12,7	22,23		The shedule entered is wrong
20	10	273	3,4	4,19	6,35	7,8	9,27	12,7	15,09	18,26	21,44	25,4	28,58	9,27	12,7	25,4
21	12	323,8	3,96	4,57	6,35	8,38	10,31	14,27	17,48	21,44	25,4	28,58	33,32	9,53	12,7	25,4
22	14	355,6	3,96	6,35	7,92	9,53	11,13	15,09	19,05	23,83	27,79	31,75	35,71	9,53	12,7	-
23	16	406,4	4,19	6,35	7,92	9,53	12,7	16,66	21,44	26,19	30,96	36,53	40,49	9,53	12,7	-
24	18	457	4,19	6,35	7,92	11,13	14,27	19,05	23,83	29,36	34,93	39,67	45,24	9,53	12,7	-
25	20	508	4,78	6,35	9,53	12,7	15,09	20,62	26,19	32,54	38,1	44,45	50,01	9,53	12,7	-
26	22	559	4,78	6,35	9,53	12,7	-	22,23	28,58	34,93	41,28	47,63	53,98	9,53	12,7	-
27	24	610	5,54	6,35	9,53	14,27	17,48	24,61	30,96	38,89	46,02	52,37	59,54	9,53	12,7	-
28	26	660	-	7,92	12,7	15,88	-	-	-	-	-	-	-	9,53	12,7	-
29	28	711	-	7,92	12,7	-	-	-	-	-	-	-	-	9,53	12,7	-
30	30	762	6,35	7,92	12,7	15,88	-	-	-	-	-	-	-	9,53	12,7	-
31	32	813	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-	9,53	12,7	-
32	34	864	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-	9,53	12,7	-
33	36	914	-	7,92	12,7	15,88	19,05	-	-	-	-	-	-	9,53	12,7	-
34	38	965	-	-	-	-	-	-	-	-	-	9,53	12,7	-
35	40	1016	-	-	-	-	-	-	-	-	-	9,53	12,7	-
36	42	1067	-	-	-	-	-	-	-	-	-	9,53	12,7	-
	44	1118	-	-	-	-	-	-	-	-	-	9,53	12,7	-
	46	1168	-	-	-	-	-	-	-	-	-	9,53	12,7	-
39	48	1219	-	-	-	-	-	-	-	-	-	9,53	12,7	-

	Carbon steel pipes
	dn	Sc -
	in
	1/2	5
	3/4	10
	1	20
	1 1/2	30
	2	40
	3	60
	4	80
	5	100
	6	120
	8	140
	10	160
	12	STD
	14	XS
	16	XXS
	18
	20
	22
	24
	26
	28
	30
	32
	34
	36
	38
	40
	42
	44
	46
	48

## 7.SS_Imp
NOMINAL SIZE	NOMINAL O.D	5S	10S	40S	80S
	mm	di [mm]	di [mm]	di [mm]	di [mm]
Stainless Steel Pipe Schedule
ANSI B36.10
dn	de	Internal diameter [mm]						Application			Dn =	1,5	in
1/8	10,29	-	7,81	6,83	5,47			(with input validation)			SCH =	5S
1/4	13,72	-	10,42	9,24	7,68			di =	Pipe_Imp_SS_Dint_Dn_SCH			44,96	mm
3/8	17,15	-	13,85	12,53	10,75			de =	Pipe_Imp_SS_Dext_Dn			48,26	mm
1/2	21,34	18,04	17,12	15,80	13,88			s =	Pipe_Imp_SS_Thickness_Dn_SCH			1,65	mm
3/4	26,67	23,37	22,45	20,93	18,85
1	33,40	30,10	27,86	26,64	24,30
1 1/4	42,16	38,86	36,62	35,04	32,46			Application			Dn =	1,5	in
1 1/2	48,26	44,96	42,72	40,90	38,10			(without input validation)			SCH =	5S
2	60,33	57,03	54,79	52,51	49,25			di =	Pipe_Imp_SS_Dint_Dn_SCH			44,96	mm
2 1/2	73,03	68,81	66,93	62,71	59,01			de =	Pipe_Imp_SS_Dext_Dn			48,26	mm
3	88,90	84,68	82,80	77,92	73,66			s =	Pipe_Imp_SS_Thickness_Dn_SCH			1,65	mm
3 1/2	101,60	97,38	95,50	90,12	85,44			The nominal diameter entered is wrong
4	114,30	110,08	108,20	102,26	97,18
5	141,30	135,76	134,50	128,20	122,24
6	168,28	162,74	161,48	154,06	146,34
8	219,08	213,54	211,56	202,72	193,68
10	273,05	266,25	264,67	254,51	247,65
12	323,85	315,93	314,71	304,79	298,45
14	355,60	347,68	346,04	-	-
16	406,40	398,02	396,84	-	-
18	457,20	448,82	447,64	-	-
20	508,00	498,44	496,91	-	-
22	558,80	549,24	547,72	-	-
24	609,60	598,52	596,90	-	-
30	762,00	749,30	746,16	-	-

							Note 1

dn	Sch
in	-
1/8	5S
1/4	10S
3/8	40S
1/2	80S
3/4
1
1 1/4
1 1/2
2
2 1/2
3
3 1/2
4
5
6
8
10
12
14
16
18
20
22
24
30

## Water Data
0	0,569	4,217	12,99	1000,00	1,75E-03	1,75E-06	1,35E-07	0,0061
1,85000000000002	0,574	4,211	12,22	1000,00	1,65E-03	1,65E-06	1,36E-07	0,0070		Application example
6,85000000000002	0,582	4,198	10,26	1000,00	1,42E-03	1,42E-06	1,39E-07	0,0099
11,85	0,590	4,189	8,81	1000,00	1,23E-03	1,23E-06	1,41E-07	0,0139		Input data: Temperature			t =	35	ºC
16,85	0,598	4,184	7,56	999,00	1,08E-03	1,08E-06	1,43E-07	0,0192
21,85	0,606	4,181	6,62	998,00	9,59E-04	9,61E-07	1,45E-07	0,0262		Function used				Results
26,85	0,613	4,179	5,83	997,01	8,55E-04	8,58E-07	1,47E-07	0,0353		SaturatedWaterConductivity_t			k =	0,625	W/(m*K)
31,85	0,620	4,178	5,2	995,02	7,69E-04	7,73E-07	1,49E-07	0,0471		SaturatedWaterSpecificHeat_t			Cp =	4,18	kJ/kg
36,85	0,628	4,178	4,62	993,05	6,95E-04	7,00E-07	1,51E-07	0,0622		SaturatedWaterPrandtl_t			Pr =	4,84	-
41,85	0,634	4,179	4,16	991,08	6,31E-04	6,37E-07	1,53E-07	0,0813		SaturatedWaterDensity_t			r =	993,8	kg/m3
46,85	0,640	4,18	3,77	989,12	5,77E-04	5,78E-07	1,53E-07	0,1053		SaturatedWaterAbsoluteViscosity_t			m =	7,22E-04	Pa*s
51,85	0,645	4,182	3,42	987,17	5,28E-04	5,35E-07	1,56E-07	0,1351		SaturatedWaterKinematicViscosity_t			n =	7,27E-07	m2/s
56,85	0,651	4,184	3,15	984,25	4,89E-04	4,97E-07	1,58E-07	0,1719		SaturatedWaterThermalDiffusivity_t			a =	1,51E-07	m2/s
61,85	0,656	4,186	2,88	982,32	4,53E-04	4,61E-07	1,60E-07	0,2169
66,85	0,660	4,188	2,66	979,43	4,20E-04	4,29E-07	1,61E-07	0,2715
71,85	0,664	4,191	2,45	976,56	3,89E-04	3,98E-07	1,63E-07	0,3374
76,85	0,668	4,195	2,29	973,71	3,65E-04	3,75E-07	1,64E-07	0,4163
81,85	0,671	4,199	2,14	970,87	3,43E-04	3,53E-07	1,65E-07	0,5102
86,85	0,674	4,203	2,02	967,12	3,24E-04	3,35E-07	1,66E-07	0,6213
91,85	0,677	4,209	1,91	963,39	3,06E-04	3,18E-07	1,67E-07	0,7518
96,85	0,679	4,214	1,8	960,61	2,89E-04	3,01E-07	1,68E-07	0,9045
100	0,680	4,217	1,76	957,85	2,79E-04	2,91E-07	1,68E-07	1,0133

t	k	Cp	Pr	ragua	m	n	a	Psat
ºC	W/(m*K)	kJ/(kg*K)	-	kg/m3	Pa s	m2/s	m2/s	bar	K

Saturation properties of water as a function of the temperature

## Air Data
-73,15	0,0181	1,007	0,737	1,7458	1,325E-05
-23,15	0,0223	1,006	0,72	1,3947	1,596E-05		Application example
26,85	0,0263	1,007	0,707	1,1614	1,846E-05
76,85	0,03	1,009	0,7	0,995	2,082E-05		Input data: Temperature				t =	35	ºC
126,85	0,0338	1,014	0,69	0,8711	2,301E-05
176,85	0,0373	1,021	0,686	0,774	2,507E-05		Function used					Results
226,85	0,0407	1,03	0,684	0,6964	2,701E-05		AirConductivity_t(t)				k =	0,027	W/(m*K)
276,85	0,0439	1,04	0,683	0,6329	2,884E-05		AirSpecificHeat_t(t)				Cp =	1,01	kJ/kg
326,85	0,0469	1,051	0,685	0,5804	3,058E-05		AirPrandtl_t(t)				Pr =	0,71	-
376,85	0,0497	1,063	0,69	0,5356	3,225E-05		AirDensity_t(t)				r =	1,134	kg/m3
426,85	0,0524	1,075	0,695	0,4975	3,388E-05		AirAbsoluteViscosity				m =	1,88E-05	Pa*s
476,85	0,0549	1,087	0,702	0,4643	3,546E-05		AirKinematicViscosity_t(t)				n =	1,66E-05	m2/s
526,85	0,0573	1,099	0,709	0,4354	3,698E-05		AirThermalDiffusivity_t(t)				a =	1,64999995888593E-08	m2/s
576,85	0,0596	1,11	0,716	0,4097	3,843E-05
626,85	0,062	1,121	0,72	0,3868	3,981E-05
676,85	0,0643	1,131	0,723	0,3666	4,113E-05
726,85	0,0667	1,141	0,726	0,3482	4,244E-05

t	k	Cp	Pr	ragua	m
ºC	W/(m*K)	kJ/(kg*K)	-	kg/m3	Pa s

Atmospheric air properties as a function of the temperature

## Re_HE
Re	1.000	10.000	100.000	1.000.000	He
100	0,420
200	0,140	0,6650
300	0,083	0,3195
400	0,056	0,1910
500	0,042	0,1387	0,9223
600	0,033	0,0944	0,6542
700	0,028	0,0720	0,4893
800	0,023	0,0587	0,3805
900	0,021	0,0491	0,3048
1.000	0,0184	0,0420	0,2499
2.000	0,0080	0,0143	0,0707	0,5499
3.000	0,0062	0,0080	0,0338	0,2506
4.000	0,0056	0,0062	0,0200	0,1435
5.000	0,0052	0,0057	0,0137	0,0931
6.000	0,0050	0,0056	0,0100	0,0654
7.000	0,0048	0,0054	0,0077	0,0485
8.000	0,0048	0,0053	0,0070	0,0374
9.000	0,0046	0,0051	0,0068	0,0298
10.000	0,0045	0,0050	0,0067	0,0243
20.000	0,0039	0,0044	0,0059	0,0083
30.000	0,0036	0,0040	0,0054	0,0063
40.000	0,0034	0,0038	0,0052	0,0056
50.000	0,0032	0,0036	0,0049	0,0054
60.000	0,0031	0,0035	0,0048	0,0052
70.000	0,0030	0,0034	0,0046	0,0050
80.000	0,0029	0,0034	0,0045	0,0049
90.000	0,0029	0,0033	0,0044	0,0047
100.000	0,0028	0,0032	0,0043	0,0046
200.000	0,0025	0,0028	0,0038	0,0040
300.000	0,0023	0,0026	0,0035	0,0037
400.000	0,0022	0,0025	0,0033	0,0035
500.000	0,0021	0,0024	0,0032	0,0033
600.000	0,0021	0,0023	0,0031	0,0032
700.000	0,0020	0,0022	0,0030	0,0031
800.000	0,0020	0,0022	0,0029	0,0030
900.000	0,0019	0,0021	0,0029	0,0030
1.000.000	0,0019	0,0021	0,0028	0,0029

## Index
				rev.cjc.09.08.2018

Index					Blower_Air_line
				www.piping-tools.net
0.- Schema					cjcruz[at]piping-tools.net
Schema of the system

1.- Air blown line					4.- SG
Input data, equations and calculation table					Main page			Specific gravity

2. Nozzle and Wye DP					Page			5.- Nm3
Pressure change in a fitting due to deceleration					1 of 8			Real flow rate to normal flow rate
Pressure loss in a diverging nozzle with cental angle q <= 45 º					2 of 8
Pressure loss in a nozzle					3 of 8			6. Blowers
Expansion in a diverging nozzle					4 of 8			Types and efficiency
Pressure loss in a converging Wye, from branch to main.					5 of 8
Expansion from Node 7 to 8					6 of 8			7. Blower
Pressure loss in a converging Wye, from main to main.					7 of 8			Blower discharge temperature
Crane equations					8 of 8
				References
3.- K-expansion
Abrupt and gradual expansion

## 0. Schema
				Number of blowers: 2 + 1

				1	Silencer discharge in a 24" pipe (batery limit)
				11					1-2	Enlargement 24" a 36"
25 . Discharge point					2-3	Pipe
				12					3-4	Butterfly valve
				16	15					10					4-5	Pipe
				25				13				9	in					5-6:	Curve 45° (5 D)
			24				14					40					6-7	Pipe
			23		17					8					7-8	Converging Wye 45º round, Branch
				18					8-9	Pipe
			22					7	in					9-10	Converging Wye 45º round, Main
				19					Blower 3				36					10-11	Pipe
			21					11-12	Curve 90° (5 D)
				20					Blower 2			6					12-13	Pipe
				5					13-14	Curve 90° (5 D)
				14-15	Pipe
				4					15-16	Curve 90° (5 D)
				16-17	Pipe
				31					17-18	Curve 90° (5 D)
				2		in				18-19	Pipe
				36				19-20	Curve 90° (5 D)
				Pblower_out / batery limit					20-21	Pipe
				in				21-22	Curve 90° (5 D)
				1		24				22-23	Pipe
				Silencer 24"					23-24	Curve 90° (5 D)
				24-25	Pipe
				25	Discharge

				Blower 1

				Schema of blower line

## 1.- Air blown line
				Return to index					rev.cjc.09.08.2018					Unhide columns to see singular pressure
Air Blown Line					drop coefficients / Hide columns.
				Nozzle Nodes 1 to 2. Expansion
Blower air line between blower silencer exit (Node 1) and a discharge point (Node 25). The system has three blowers with two operating at a time.					Change in pressure due to change velocities
The system is considered isothermic, since the total duct length is relatively short.					Diverging nozzle . Pressure increment
				DPkinem =	708	Pa	(Sheet. 2)
Height above sea level			H =	2600	m.a.s.l.		Flow per blower (2 + 1 ) at				Air molecular mass				Blower discharge temperature					Diverging nozzle 24x36, with cental angle
Local atmospheric press. [Eq.1]			Patm =	73,75	kPa		blower discharge				Rair =	286,9	J/(kg*K)		tblower_out =	129,6	°C	(Sheet 7)					Wye Nodes 7 to 8					q =	30	º
Blower discharge pressure			Pblower_out =	70	kPa(g)		Qblower =	650	m3/min		Molecular mass of gas (in this				T =	402,7	K					Converging Wye 45º (branche to main)					Pressure loss coefficient			(Sheet. 2)
(at silencer exit. Node 1)			Pblower_out =	143,7	kPa		Qblower =	39.000	m3/h		case is air)				Since the temperature is constant, the					Change in pressure due to change in velocities					K2 =	1,068
			Pblower_out =	143.749	Pa		Qtotal =	Qblower * 2			Rgas =	286,9	J/(kg*K)		absolute viscosity will be constant.					40
Maximum allowed pressure drop			DPmax =	1,5	kPa		Qtotal =	1.300,0	m3/min		Absolute rugosity				Air absolute viscosity					Wye Nodes 9 to 10
Minimum required pressure			Pdisc_min =	142,2	kPa		Qtotal =	78.000	m3/h		Rabs =	0,15	mm		m =	AirAbsoluteViscosity_t					36				[10] Page 35.9
(at ring inlet. Node 25 )			Pdisch_min =	68,5	kPa(g)					Rabs =	0,00015	m		m =	2,31219000852434E-05	Pa s					36			Straight (main) section
				Galvanized steel sheet thickness					DP =	Cs * Pkinem	Eq. (30)
				selected Gauge :		14					DPkinem =	60	Pa	(Sheet. 2)
				s =	2,0	mm [4]					Pressure loss coefficient			(Sheet. 2)
				K2 =	1,133
Equations
Eq. 1				Eq. 4				Eq. 7				Eq. 10				Eq 13					Wye Nodes 9 to 10
Local atmospheric temperature				Kinematic pressure				Reynolds number				Singular pressure drop coefficient				Total pressure change					Converging Wye 45º (main to main)
Patm = 101.325* (1 -0.0000225577 * E4)^5.25588				hv =	(r/2) * v^2		(Pa)	Re =	v * d / n			Ksing =	SUMPRODUCTO(range_A*range_B)			DP =	DPf+DPs					Change in pressure due to change in velocities
			(kPa)
Eq. 2				Eq. 5				Eq. 8				Eq.11				Eq. 14
Air density				Kinematic viscosity				Friction factor				Singular pressure drop				Pressure at the exit node					40	40			'From '2. Nozzle and Wye DP'!, S279, S280 and S281
r =	P / (Rair * T)		(kg/m³)	n =	m / r		(m²/s)	f =	Pipe_Friction_Factor_Rrel_Re			DPs =	Ksing * hv		(Pa)	Pout =	Pin - DP					As / Ac =	1
				Ab / Ac =	0,809
Eq. 3				Eq. 6				Eq. 9				Eq.12				Average value of the friction factor					Qs / Qc =	0,5
Inside duct diameter				Relative rugosity				Friction pressure loss				DPk: Pressure increment due to deceleration				fave =	0,0133	-					DPkinem =	-112	Pa	(Sheet. 2)		From table in Ref. 10
di =	dn * 25.4 - 2*s		(m)	Rrel =	Rabs / d		(-)	DPf =	f * (L/d) * hv		(Pa)	(Sheet 7. Nozzle, sheet 2 Wye)					(Fluid is accelerated)					Pressure loss coefficient			(Sheet 2)
				Cs =	0,06
Calculation table for the nodes of the blower line					Nozzle	Wye	Wye
				1 to 2	7 to 8	9 to 10
				Curve 90º (5D)	Curve 45º(5D)	Tee br 45°	Tee str 45°	24	36	40	V. Butterfly
				Eq.2		Eq. 3				Eq. 4	Eq. 5	Eq. 6	Eq. 7	Eq. 8	Eq. 9					36	40	40		Eq. 10	Eq. 11	Eq. 12	Eq. 13	Eq. 14
				Qact		Pin	r	dn	di	L	A	v	hv	n	Rrel	Re	f	DPf	0,00	0,00	1,16	0,13	1,068	1,133	0,060	0,098	Ksing	DPs	DPk	DP	Pout
Description			Node	Node	m3/h	m3/s	Pa	kg/m3	in	m	m	m²	m/s	Pa	m²/s	-	-	-	Pa					Pa	Pa	Pa	Pa	kPa(g)
Enlargement (24x36)			1	2	39.000	10,8	143.749	1,24	24	0,61	0,0	0,288	37,6	172,3	1,9E-05	0,0002	1,2E+06		0,0					1				1,07	184	-708	-524	144273	70,52
Pipe			2	3	39.000	10,8	144.273	1,25	36	0,91	4,0	0,651	16,64	172,9	1,9E-05	0,0002	8,2E+05	0,014	11,0					0,00	0		11	144262	70,51
V. Butterfly			3	4	39.000	10,8	144.273	1,25	36	0,91	0,0	0,651	16,6	172,9	1,9E-05	0,0002	8,2E+05		0,0					1	0,10	17		17	144245	70,50
Pipe			4	5	39.000	10,8	144.245	1,25	36	0,91	4,0	0,651	16,6	172,9	1,9E-05	0,0002	8,2E+05	0,014	11,0					0,00	0		11	144234	70,48
Curve 45° (5 D)			5	6	39.000	10,8	144.245	1,25	36	0,91	0,0	0,651	16,6	172,9	1,9E-05	0,0002	8,2E+05		0,0		1					0,00	0		0	144234	70,48
Pipe			6	7	39.000	10,8	144.234	1,25	36	0,91	4,0	0,651	16,6	172,9	1,9E-05	0,0002	8,2E+05	0,014	11,0					0,00	0	0	11	144223	70,47
Converging Wye 45º round, Branch			7	8	39.000	10,8	144.234	1,25	36	0,91	0,0	0,651	16,6	113,2	1,9E-05	0,0002	8,2E+05		0,0					1			1,13	128	60	188	144035	70,29
Pipe			8	9	39.000	10,8	144.223	1,25	40	1,01	20,0	0,804	13,5	113,2	1,9E-05	0,0001	7,4E+05	0,014	32,2					0,00	0		32	144002	70,25
Converging Wye 45º round, Main			9	10	78.000	21,7	144.002	1,25	40	1,01	0,0	0,804	26,9	452,2	1,9E-05	0,0001	1,5E+06		0,0					1		0,06	27	112	139	143863	70,11
Pipe			10	11	78.000	21,7	143.863	1,25	40	1,01	40,0	0,804	26,9	451,7	1,9E-05	0,0001	1,5E+06	0,014	245,4					0,00	0		245	143618	69,87
Curve 90° (5 D)			11	12	78.000	21,7	143.618	1,24	40	1,01	0,0	0,804	26,9	451,0	1,9E-05	0,0001	1,5E+06		0,0	1					0,00	0		0	143618	69,87
Pipe			12	13	78.000	21,7	143.618	1,24	40	1,01	4,0	0,804	26,9	451,0	1,9E-05	0,0001	1,5E+06	0,014	24,5					0,00	0		24	143593	69,84
Curve 90° (5 D)			13	14	78.000	21,7	143.593	1,24	40	1,01	0,0	0,804	26,9	450,9	1,9E-05	0,0001	1,5E+06		0,0	1					0,00	0		0	143593	69,84
Pipe			14	15	78.000	21,7	143.593	1,24	40	1,01	20,0	0,804	26,9	450,9	1,9E-05	0,0001	1,5E+06	0,014	122,5					0,00	0		122	143471	69,72
Curve 90° (5 D)			15	16	78.000	21,7	143.471	1,24	40	1,01	0,0	0,804	26,9	450,5	1,9E-05	0,0001	1,5E+06		0,0	1					0,00	0		0	143471	69,72
Pipe			16	17	78.000	21,7	143.471	1,24	40	1,01	10,0	0,804	26,9	450,5	1,9E-05	0,0001	1,5E+06	0,014	61,2					0,00	0		61	143410	69,66
Curve 90° (5 D)			17	18	78.000	21,7	143.410	1,24	40	1,01	0,0	0,804	26,9	450,3	1,9E-05	0,0001	1,5E+06		0,0	1					0,00	0		0	143410	69,66
Pipe			18	19	78.000	21,7	143.410	1,24	40	1,01	6,0	0,804	26,9	450,3	1,9E-05	0,0001	1,5E+06	0,014	36,7					0,00	0		37	143373	69,62
Curve 90° (5 D)			19	20	78.000	21,7	143.373	1,24	40	1,01	0,0	0,804	26,9	450,2	1,9E-05	0,0001	1,5E+06		0,0	1					0,00	0		0	143373	69,62
Pipe			20	21	78.000	21,7	143.373	1,24	40	1,01	20,0	0,804	26,9	450,2	1,9E-05	0,0001	1,5E+06	0,014	122,3					0,00	0		122	143251	69,50
Curve 90° (5 D)			21	22	78.000	21,7	143.251	1,24	40	1,01	0,0	0,804	26,9	449,8	1,9E-05	0,0001	1,5E+06		0,0	1					0,00	0		0	143251	69,50
Pipe			22	23	78.000	21,7	143.251	1,24	40	1,01	5,0	0,804	26,9	449,8	1,9E-05	0,0001	1,5E+06	0,014	30,5					0,00	0		31	143220	69,47
Curve 90° (5 D)			23	24	78.000	21,7	143.220	1,24	40	1,01	0,0	0,804	26,9	449,7	1,9E-05	0,0001	1,5E+06		0,0	1					0,00	0		0	143220	69,47
Pipe			24	25	78.000	21,7	143.220	1,24	40	1,01	2,0	0,804	26,9	449,7	1,9E-05	0,0001	1,5E+06	0,014	12,2					0,00	0		12	143208	69,46
				fave =	0,0140					OK. Pexit > Pdisch_min

				Return to index					Pdisch_min =	68,50	kPa(g)
				Converging Wye (45º) round (nodes 7 to 8)
				Number of blowers: 2 + 1
				QA =	0	m³/s		QC =	10,8		m³/s
				vA =	0	m/s		vC =	13,5		m/s
				11					AA =	0,651	m²		AC =	0,804		m²
	25 . Discharge point
				12
				16	15					10
				25				13				9	in					QB =	10,8	m³/s
				24				14					40					vB =	16,6	m/s
				23		17					8					AB=	0,651	m²
				18
				22					7	in
				19					Blower 3				36					Branch, Cc,b
				21
				20					Blower 2			6					vB /vC =
				5					vB =	16,6	m/s
				vC =	13,5	m/s
				4					vB /vC =	1,24	-
				Silencer 24" / Pblower_out / batery limit / Blower 1 / 1 / 2 / 31 / in / in
				AB /AC =
				36				AB =	0,651	m²
				AC =	0,804	m²
				24				AB /AC =	0,81

				A / B / C	From Fig. 6.2, [3], page 33.40
				for:
				vB /vC =	1,24
				AB /AC =	0,81
				one obtains with interpolation
				Cc,b =	1,16

				Converging Wye (45º) round (nodes 9 to 10)
				Schema of blower line
				QA =	10,8	m³/s		QC =	21,7		m³/s
				vA =	13,5	m/s		vC =	26,9		m/s
				AC =	#REF!	m²
				AB /AC =	#REF!
1	Silencer discharge in a 24" pipe (batery limit)					13-14	Curve 90° (5 D)					g =	9,80665		m/s²
1-2	Enlargement 24" a 36"					14-15	Pipe					From Fig. 6.2, [3], page 33.40
2-3	Pipe					15-16	Curve 90° (5 D)					for:
3-4	Butterfly valve					16-17	Pipe					vB /vC =	#REF!
4-5	Pipe					17-18	Curve 90° (5 D)					AB /AC =	#REF!
5-6:	Curve 45° (5 D)					18-19	Pipe					one obtains with interpolation
6-7	Pipe					19-20	Curve 90° (5 D)					Cc,b =	0,125
7-8	Converging Wye 45º round, Branch					20-21	Pipe
8-9	Pipe					21-22	Curve 90° (5 D)
9-10	Converging Wye 45º round, Main					22-23	Pipe					Cross section to which coefficients is referenced:
10-11	Pipe					23-24	Curve 90° (5 D)					the common section (C)
11-12	Curve 90° (5 D)					24-25	Pipe
12-13	Pipe					25	Discharge					hvC=	(r/2) * vC^2 [Pa]

				Pressure loss through the branch
				DPBC =	Cc,b * hvC

				Pressure loss through the main (stright)
				DPAC =	Cc,s * hvC

## 2. Nozzle and Wye DP
				Return to index			rev.cjc.09.08.2018
				Page 1 of 10
		Pressure change in a fitting due to deceleration

		Applicable to any shape					P1 / v1 / P2 / v2 / z1 / z2 / q/2 / Figure 1

				Kinematic pressure change due to
				velocity change between two sections
				of a fitting

				Page 2 of 10

				Page 3 of 10
				P1 / v1 / P2 / v2 / z1 / z2 / q/2 / Figure 1

2					Return to index
				Page 4 of 10
				Kinematic pressure change				and the pressure loss in the diverging
		Pressure loss in a diverging nozzle with					nozzle with central angle q <= 45º
		cental angle q <= 45 º

				An application of this pressure loss for a diverging nozzle
				is shown in this sheet, Page 3 of 5.

				Pressure loss in a Round Converging Wie (45º)

				Total pressure increment in a diverging
				nozzle for a central angle q <= 45º

				with the kinetic pressure increment due
				to the deceleration				The singular pressure loss coeficient is obtained from a table from
				Ashrae Handbook 1985 Fundamentals [3], Figure 6.2, page 33.40
				The table is shown in sheet Ref. 3

				An application of the use of this table is shown in this sheet,
				Page 4 of 5

				Return to index
				Page 5 of 10
		Pressure loss in a nozzle, according [9]

		If q <= 45 º					If 45º < q <= 180 º
		Let					Let
		q =	30	°				q =	50	°

		K2 =	(2.6 * ( seno(radianes(q)/2) ) * (1 - b^2)^2) / b^4					K2 =	(1 - b^2)^2/ b^4
		b =	0,66		bmin =	0,7		b =	0,6600		bmin =	0,7
		K2 =	1,130					K2 =	1,679

		DP =	K2 * hv_2					DP =	K2 * hv_2
		K2 =	1,130					K2 =	1,679
		hv_2 =	150,0	Pa				hv_2 =	150,0	Pa
		DP =	169	Pa				DP =	252	Pa

				Return to index
				Page 6 of 10
		Expansion in a diverging nozzle
		24x36	Node 1 to 2		dn_out =	36	in	Density in larger section			Nozzle pressure loss
		Pressure increment in a nozzle due to			s =	2,0066		Since at this moment only the density in			hv_2, refered to the common section
		area increment. Central angle "q"			dout =	910,3868	mm	section 1 is known, it will be assumed			DPLoss =	K2 * hv_2
	P1 / v1 / P2 / v2 / z1 / z2 / q/2				dout =	0,9104	m	r2 =	r1		K2 =	1,068
				From sheet 1			hv_2 =	172,3	Pa
				dlarge =	0,9104	m²	r1 =	1,24	kg/m³	DPLoss =	184	Pa
				Area of larger section			r2 =	1,24	kg/m³	Pressure decrement
				Alarge =	(p/4) * dlarge^2
				Alarge =	0,651	m²				(Equation from sheet 3)
				Velocity pressure in larger section
				b =	dmin / dmax		hv_2 =	(r/2) * v^2	[Pa]
				dout =	0,606	m	r =	1,24	kg/m³
		q =	30	º	din =	0,910	m	v2 =	16,64	m/s
				b =	0,6652		hv_2 =	172	[Pa]
		Flow rate
		Q =	10,83	m3/s	Velocity in larger section			Single pressure loss coefficient, using
				vlarge_sect =	Q / Alarge		the equation			Pressure increment
		Pipes			Q =	10,83	m3/s	K2 = (2.6*(seno(radianes(q)/2))*(1-b^2)^2) / b^4			DPkinem =	(r/2) * v2^2 * ( 1/b^4 -1 )			Note
		dn_in =	24	in	Alarge =	0,651		q =	30	º	r =	1,24	kg/m3		The coefficient K2 corresponds to
		s =	2,0066		vlarge_sect =	16,64	m/s	b =	0,6652	-	v2 =	16,64	m/s		the conditions at the largest
		din =	605,5868	mm				K2 =	1,068	-	b =	0,6652			diameter, which in this case is d2.
				Used in '1.- Air blown line '!AG15			DPkinem =	708	Pa
		din =	0,6056	m					Used in '1.- Air blown line '!AG11

				Return to index
				Page 7 of 10
		Pressure loss in a converging Wye, from branch to main.

		Node 7 to 8
		Converging Wye (45º) round

		QA =	0	m³/s		QC =	10,8	m³/s
		vA =	0	m/s		vC =	13,5	m/s
		AA =	0,651	m²		AC =	0,8	m²
			A / B / C

			QB =	10,8	m³/s
			vB =	16,6	m/s
			AB=	0,7	m²					[3]

			Branch, BC

			vB /vC =
			vB =	16,6	m/s	From Fig. 6.2, [3], page 33.40
			vC =	13,5	m/s	for:
			vB /vC =	1,24	-	vB /vC =	1,24
				AB /AC =	0,81
			AB /AC =			one obtains with interpolation
			AB=	0,651	m²	Cc,b =	1,133
			AC =	0,804	m²	Used in '1.- Air blown line '!AG17
			AB /AC =	0,809

			Interpolation table
				0,8	0,809	1			1,24
			1	0,62		0,69
			1,24	1,129	1,133	1,213
			1,5	1,7		1,8

				Return to index
				Page 8 of 10
		Expansion from Node 7 to 8 / x
		36	40		dn_out =	40	in	Density in larger section
		Pressure increment due to			s =	2,0066		Since at this moment only the density in
		area increment.			dout =	1011,9868	mm	section 1 is known, it will be assumed
				dout =	1,0120	m	r2 =	r1
	P1 / v1 / P2 / v2					From sheet 1
				dlarge =	1,0120	m²	r1 =	1,25	kg/m³		Increment
				Area of larger section			r2 =	1,25	kg/m³		DPkinem =	(r/2) * v2^2 * ( 1/b^4 -1 )
				Alarge =	(p/4) * dlarge^2		Check:	OK			r =	1,25	kg/m3
				Alarge =	0,804	m²					v2 =	13,47	m/s
				b =	0,8996
				Diameters ratio			Velocity pressure in larger section				DPkinem =	60	Pa
				b =	dmin / dmax		hv_2 =	(r/2) * v^2	[Pa]		Used in '1.- Air blown line '!AG15
				dout =	0,910	m	r =	1,25	kg/m³
		Flow rate			din =	1,012	m	v2 =	13,47	m/s
		Q =	10,83	m3/s	b =	0,8996		hv_2 =	113	[Pa]
			(Sheet 1)
				Velocity in larger section			Singular fricction factor
		Pipes			vlarge_sect =	Q / Alarge		Circular Diverging Wye
		dn_in =	36	in	Q =	10,83	m3/s	K2 =	1,133	(sheet 2)
		s =	2,0066		Alarge =	0,804			Pressure decrement
		din =	910,3868	mm	vlarge_sect =	13,47	m/s
				Note
		din =	0,9104	m				The coefficient K2 corresponds to the conditions at
				the largest diameter, which in this case is d2.

				Return to index
				Page 9 of 10
		Pressure loss in a converging Wye, from main to main.

		Converging Wye (45º) round . Nodes 9 to 10

		QS =	10,8	m³/s		QC =	21,7	m³/s
		vS =	13,5	m/s		vC =	26,9	m/s
		AS =	0,804	m²		AC =	0,804	m²
			A		C
				B

			QB =	10,8	m³/s	Same data as 7-8
			vB =	16,6	m/s
			AB=	0,7	m²

		AS /AC =
		AS=	0,804	m²
		AC =	0,804	m²
		AS /AC =	1,000
		AB /AC =				Kinematic pressure change due to
		AB=	0,65			velocity change between two sections					As / Ac =	1,000
		AC =	0,80			of a fitting					Ab / Ac =	0,809
		AS /AC =	0,81					Qs / Qc =	0,5
		QS /QC =
		QS =	10,8	m/s
		QC =	21,7	m/s		DPkinem =	(r/2) * (v1^2 - v2^2
		QS /QC =	0,50	-		r =	1,25	kg/m³
		[10], Table ED5-2 Wye, 45º, converging, page 35.37				v1 =	13,5	m/s
		straight (main) section)		(Sheet Ref. 10		v2 =	26,9	m/s
		DP =	Cs * Pkinem	Eq. (30)		DPkinem =	-112,2	Pa
		Cs =	0,06
		Used in '1.- Air blown line AL32

				Return to index
				Page 10 of 10
		Crane equations [9]

## 3.- K-expansion
				Return to index					rev.cjc.09.08.2018
	Abrupt and gradual expansion [9]
				Example					Example
				For enlargements with q > 45°					Expansion between two ducts					Expansion between two ducts
				with b >= 0.7
				K2 =	(1 - b^2) / b^4					Inlet duct diameter					Inlet duct diameter
		d1	q			d2					dn_in =	24	in			dn_in =	24	in
				Outlet duct diameter					Outlet duct diameter
				b =	0,7					dn_out =	36	in			dn_out =	36	in
				K2 =	2,1241					Center angle					Center angle
				q =	30	º			q =	25	º

				Sheet thickness					Sheet thickness
				s =	2,0066	mm			s =	2,0066	mm

	If q <= 45 º					If 45º < q <= 180 º					Inlet section					Inlet section
				dn_in =	24	in			dn_in =	24	in
				s =	2				s =	2,0066
				din =	605,6	mm			din =	605,5868	mm
				din =	0,6056	m			din =	0,6056	m

				Outlet section					Outlet section
				dn_out =	36	in			dn_out =	36	in
	K2 =	(2.6 * ( seno(radianes(q)/2) ) * (1 - b^2)^2) / b^4					K2 =	(1 - b^2)^2/ b^4					s =	2,0066				s =	2,0066
	q =	30	º					dout =	910,3868	mm			dout =	910,3868	mm
	b =	0,665		bmin =	0,6		b =	0,665					dout =	0,9104	m			dout =	0,9104	m
	K2 =	1,071		(See graphic, below)			K2 =	1,591
				Diameters ratio					Diameters ratio
				b =	dmin / dmax				b =	dmin / dmax
	Note. Coefficients refered to the velocity of larger pipe (Index 2)					dout =	0,910	m			dout =	0,910	m
				din =	0,606	m			din =	0,606	m
				b =	0,6652				b =	0,6652

				Single pressure loss coefficient, using					Single pressure loss coefficient, using
				the VBA function for q = 30 º					the equation
				K2 = Pipe_Expansion_Theta30gr_beta					K2 = (2.6*(seno(radianes(q)/2))*(1-b^2)^2) / b^4

				q =	25	º
				b =	0,6652	-			b =	0,6652	-
				K2 =	1,068	-			K2 =	0,893	-

	Using the VBA function
	K2 =	Pipe_Expansion_Theta30gr_beta
	b =	0,707
	K2 =	0,674

	q =	30	º

	b =	K2 =
Singular coefficient / beta / K	0,05
	0,10
	0,15
	0,20
	0,25
	0,30	68,80
	0,35	34,53
	0,40	18,55
	0,45	10,44
	0,50	6,06
	0,55	3,58
	0,60	2,13
	0,65	1,26
	0,70	0,73
	0,75	0,41
	0,80	0,21
	0,85	0,10
	0,90	0,04
	0,95	0,01
	1,00	0,00

## 4.- SG
				Return to index				rev.cjc.09.08.2018

	Specific gravity

	The SG-value is required in Sheet 6, for				In the US gas industry typical references				K value for gas valve
	the calculation of the K-value for the				conditions are:				The calculation of the Pressure drop
	selected valve type.				PStd =	1	atm		coefficient K for the valve requires as
				tStd =	60	ºF		an input, the specific gravity of the gas.
	Specific gravity of gas					This K coefficient is calculated using
	Molecular mass of air				Air density at				equation 8c (See note 2)
	MMair =	286,90	J/(kg*K)		PStd =	101325	Pa
		(Sheet 1)			tStd =	15,6	ºC
	Molecular mass of gas				T =	288,7	K
	MMgas =	286,9	J/(kg*K)		Molecular mass
		(Sheet 1)			M =	28,97	kg/kmol		Base Gas Density
	SG =	MMgas / MMair			Gas general constat				The gas density equation remains the same but is referenced to what are known as standard
	MMgas =	286,90	J/(kg*K)		Rg =	8314,41	J/kmol K		temperature and pressure conditions (STP). The reference conditions used in general industry
	MMair =	286,90	J/(kg*K)					are 60ºF and 14.696 PSIA. The reference conditions used vary from country to country and
	SG =	1	-		Density				from industry to industry. In the U.S. gas industry typical reference conditions are 60ºF and
				rair_Std =	p * M / ( Rg *T )			14.73 PSIA.
	Since in this application the gas is air, the				p =	101325	Pa
	calculation is inofficious				M =	28,97	kg/kmol		www.piping-tools.net
				Rg =	8314,41	J/kmol K		Valves. Pressure loss in valves with gas as a fluid. Normal and choked flow (SI)
				T =	288,7	K		and using VBA function
				rair_Std =	1,22	kg/m3		Pipe_Valve_K_Gas_PinBarAbs_SG_QNm3h_HvPascal_Cv_toutCelcius

Specific Gravity for Gases

The Specific Gravity of a gas is normally calculated with reference to air - and defined as the ratio of the density of the gas to the density of the air - at a specified temperature and pressure.

The Specific Gravity can be calculated as

SG = ρgas / ρair (3)					tnormal =	20	ºC
				tnormal =	68	ºF
where

SG = specific gravity of gas					Normal pressure and temperature of gases Imperial system

ρgas = density of gas (kg/m3)

ρair = density of air (normally at NTP - 1.205 kg/m3)

NTP - Normal Temperature and Pressure - defined as 20oC (293.15 K, 68oF) and 1 atm ( 101.325 kN/m2, 101.325 kPa, 14.7 psia, 0 psig, 30 in Hg, 760 torr)

Molecular weights can be used to calculate Specific Gravity if the densities of the gas and the air are evaluated at the same pressure and temperature.

## 5.- Nm3
				Return to index			rev.cjc.09.08.2018

Real flow rate to normal flow rate

Real flow rate data					Normal volumetric flow rate, Eq. (a)
V =	10,83	m³/s	(Sheet 1)		Vn =	(Pop/Pn) * (Tn/Top) * V
V =	39.000	m3/h			Pop =	144.273	Pa
Pop =	1,4	bar	(Sheet 1)		Pn =	101.325	Pa
top =	130	°C	(Sheet 1)		Tn =	273,15	K
				Top =	402,72	°C
Normal conditions					V =	39.000,0	m3/h
Pn =	101.325	Pa			Vn =	37.665	Nm3/h
Tn =	273,15	K

Operation absolute temperature
Top =	top + 273.15				Note
top =	129,6	°C			For the deduction of equation (a), see
Top =	402,72	K			www.piping-tools
				File: Normal_to_real_flow_rate_and_FAD_flow rate
Pop =	144.273	Pa

Kelv =	273,15	K

## 6. Blowers
http://onlinembr.info/cost/blower-power-calculation-blower-types-and-efficiency/

## 7. Blower disch. temp.
			Return to index					rev.cjc.09.08.2018

Blower discharge temperature

Specific heat ratio
k =	1,4	-		Inlet temperature				Discharge temperature of a real compresión
Local atmospheric pressure				Tin =	283,15	K		Tdesc =	Tin + (Tdesc_s - Tin) / hc
Patm_loc =	73,7	kPa		Intake pressure				Tin =	283,15	K
Average ambient temperature				Pin =	Patm_loc			Tdisch_s =	343	K
tin =	10	°C		Pin =	73,7	kPa		hcomp =	0,50	-
Fan efficiency				Discharge pressure				Tdisch =	403	K
hc =	0,50			Pout =	Patm_loc + Pdisch			tdisch =	129,6	ºC
Discharge manometric pressure				Patm_loc =	73,7	kPa
Pdisch =	70	kPa(g)		Pdisch =	70,0	kPa(g)		Also
				Pout =	143,7	kPa		Tdisch =	Tin * ( 1 + ( ((Pdesc/Pin)^((k-1)/k) -1) / hc ) )
				Discharge temperature				Tin =	283,15	K
				of isentropic compresión				Pout =	143,7	kPa
				Tdisch_s =	Tin * (Pout/Pin)^((k-1)/k)			Pin =	73,7	kPa
				Tin =	283,15	K		k =	1,4	-
				Pin =	73,7	kPa		hc =	0,50	-
				Pout =	143,7	kPa		Tdisch =	403	K
				k =	1,4	-		tdisch =	129,6	ºC
				Tdisch_s =	343	K

## Ref
				Return to Index

[1]	www.piping-tools.net

[2]	Norris butterfly valves
	http://www.norriseal.com/files/comm_id_47/BV_HowTo_Brochure_120811.pdf

[3]	Ashrae Handbook 1985 Fundamentals

[4]	http://www.engineeringtoolbox.com/gauge-sheet-d_915.html

[9]	Crane Co., Flow of Fluids Through Valves, Fittings and Pipe. Technical Paper No. 410M, 21st printing. Crane Co., 300 Park Ave., New York (1982).

[10]	Ashrae Handbook 2005 Fundamentals

	[14]

		http://www.forberg.com/pdf/techSup/Home_Tech%20Support_Valve%20Flow_calc_and_sizing.pdf

## Ref. 3
Singular pressure drop coefficient for a round, 45º, converging wye [3]
					[3], page 33.5
					Galvanized steel, sheets, hot
					A / B / C / vC / AC / vB / AB					dipped longitudinal seams
					Rabs =	0,15	mm

					Ashrae Handbook 1985 Fundamentals [3], Figure 6.2, page 33.40

					Cross section to which coefficients is referenced: the common section (C)
					[3], page 33.39.

					hvC=	(r/2) * vC^2 [Pa]

					Pressure loss through the branch
					DPBC =	Cc,b * hvC

					Pressure loss through the main (stright)
					DPAC =	Cc,s * hvC

## Ref.4
Thickness of galvanized steel sheets				[4]

									Galvanized Steel
									Gauge	Thickness
									in	mm
									20	0,04	1,016
									19	0,046	1,1684
									18	0,052	1,3208
									17	0,058	1,4732
									16	0,064	1,6256
									15	0,071	1,8034		Galvanized steel sheet
									14	0,079	2,0066		Gauge	14	-
									13	0,093	2,3622		thickness	2,007	mm
									12	0,108	2,7432
									11	1,123	28,5242
									10	0,138	3,5052
									9	0,153	3,8862
									8	0,168	4,2672

## Ref. 10
Wye, 45 degree
Ashrae 2005, page 35.9

					[10] Page 35.9
					straight (main) section
					DP =	Cs * Pkinem	Eq. (30)

	straight (main) section

					[10] Page 35.9
					straight (main) section
					DP =	Cs * Pkinem	Eq. (30)

					As / Ac =
					Ab / Ac =
					Qs / Qc =

					From table
					Cs =

	From [10], Table ED5-2 Wye, 45º, converging, page 35.37

					[10] Page 35.9
					straight (main) section
					DP =	Cs * Pkinem	Eq. (30)

					As / Ac =	1
					Ab / Ac =	0,809286337677569
					Qs / Qc =	0,5

					From table
					Cs =	0,06

## Ref. 14
[4]	http://www.forberg.com/pdf/techSup/Home_Tech%20Support_Valve%20Flow_calc_and_sizing.pdf					Return to 14. Gas valves

				1 psi =	6894,76	Pa

	Choked flow. Example 2
	dn =	1/4	in
	Pin =	3000	psig
	t =	600	ºF
	Qmin_req =	325	scfm
	Valve:	Parker 4V1-DP4R-SSP-C4
	Cv =	0,31	[gpm/psi^0.5]
	From Table 2
	SG =	1,183	-

	Find the maximum possible flow rate
	Thus, choked glow equation will be used
	The condition for choked flow is approx
	Pout =	Pin / 1.89

	Atmospheric pressure
	Pin =	Pin + Patm

	Pin =	3000	psig
	Patm =	14,7	psi
	Pin =	3014,7	psia

	Pout =	Pin / 1.89
	Pin =	3014,7	psia
	Pout =	1595	psia

	T =	t + Rank
	t =	600	ºF
	T =	1059,67	R

	Q(scfm) =	13.63 * Cv * Pin(psia) * ( T(R) * SG )^-0.5
	Cv =	0,31
	Pin =	3014,7	psia
	T =	1059,67	R
	SG =	1,183	-
	Q(scfm) =	359,8	scfm
	Qmin_req =	325	scfm
	OK. Qmax > Qmin_req

				1 psi =	6894,76	Pa
				1 Scfm =	1,5831	Nm3/h

				Cv :	[gpm/psi^0.5]

				0

		Imperial standard flow rate to Normal flow rate					Standard cubic feet a minute @ 68 ªF

		Imperial standard flow rate data				Normal absolute pressure					1 ft =	0,3048	m
				PN =	101.325	Pa				1 ft ³ =	0,02832	m³
		VS =	1,0	Sm3/h		Normal absolute temperature					1 ft ³/min =	0,02832	m³/min
				TN =	273,15	K				1 cfm =	0,02832	m³/min				VN =	VS * (TN / TS) * (PS / PN)
		Imperial standard temperature					1 Scfm =	0,02832	Sm³/min
		tS =	68	°F		Standard volumetric flow rate to
		tS =	20,00	°C		Normal volumetric flow rate					1 Sm3/min =	0,9318	Nm3/min
		Imperial standard pressure				Vn =	VS * (PS/Pn) * (Tn/TS)
		PS =	101.325	kPa		PS =	101.325	Pa				1 Scfm =	0,02638	Nm3/min
				Pn =	101.325	Pa				1 Scfm =	1,5831	Nm3/h
				Tn =	273,15	K
		Standard conditions (Imperial)				TS =	293,15	°C
		PS =	101.325	Pa		VS =	1,0	Sm3/h			1	m³ =	=	35,3147	ft³
		TS =	293,15	K		Vn =	0,9318	Nm3/h			1	Sm³/h	=	0,9318	Nm³/h
				35,3147	Sft³/h	=	0,932	Nm³/h
				1	Sft³/h	=	0,02638	Nm³/h
				1	Sft³/min	=	0,02638	Nm³/min
				1	Scfm =	=	0,02638	Nm³/min
				1	Scfm =	=	1,5831	Nm³/h