## I. Channels
				rev.cjc.18.08.2018

		Resume of channels using a constant Manning's coefficient

		Circular channels, normal conditions					Circular channels, critical conditions
		Semicircular channles, normal conditions					Semicircular channles, critical conditions
		Rectangular channels, normal conditions					Rectangular channels, critical conditions

Normal condictions

Circular Channel					Semicircular Channel					Rectangular Channel
Input					Input					Input
	Q =	0,5	m3/s					Q =	0,5	m3/s					Q =	0,5	m3/s
	D =	0,92054	m					D =	0,602	m					b =	1,4	m
	N =	0,0117	-					N =	0,011	-					N =	0,011	-
	S =	0,011	m/m					S =	0,02	m/m					S =	0,02	m/m

Output					Output					Output

Height	H =	Channel_Circular_Height_Q_D_N_S(Q, D, N, S)					Height	Hn =	Channel_SemiCircular_Height_Q_D_N_S(Q;D; N;S)					Height	H =	Channel_Rectangular_Height_Q_B_N_S(H4;H5;H6;H7)
	H =	0,2954	m					Hn =	0,2949	m					H =	0,1243	m

Area	A =	Channel_Circular_Area_Q_D_N_S(Q, D, N, S)					Area	A =	Channel_SemiCircular_Area_Q_D_N_S(Q; D; N; S)					Hydr. Rad.	Rh =	Channel_Rectangular_Hydraulic_Radius_Q_B_N_S
	A =	0,1843	m²					A =	0,1386	m²					Rh =	0,1056	m

TopWidth	T =	Channel_Circular_Top_Width_Q_D_N_S(Q; D; N; S)					Top width	T =	Channel_SemiCircular_Top_Width_Q_D_N_S(Q; D;N; S)					Froude	Fr =	Channel_Rectangular_Froude_Q_b_n_S
		0,859					T =	0,602	m					Fr =	2,6011	-

Froude	Fr =	Channel_Circular_Froude_Q_D_N_S(Q, D, N, S)					Froude	Fr =	Channel_SemiCircular_Froude_Q_D_N_S(Q; D; N; S)					Critical_velocity	v =	Channel_Rectangular_Velocity_Q_b_n_S
	Fr =	1,871	-					FR =	2,400	-					v =	2,8723	m/s

WettedPerimeter	P =	Channel_Circular_Wetted_Perimeter_Q_D_N_S					WettedPerimeter	P =	Channel_SemiCircular_Wetted_Perimeter_Q_D_N_S					Energy	E =	Channel_Rectangular_Energy_Q_B_N_S
	P =	1,1088					P =	0,9334	m					E =	0,5450	m

Hydraulic radius	Rh =	Channel_Circular_Hydraulic_Radius_Q_D_N_S(Q; D; N;S)					Hydraulic radius	Rh =	Channel_SemiCircular_Hydraulic_Radius_Q_D_N_S(Q; D; N; S)
	Rh =	0,1662	m					Rh =	0,1485	m

Velocity	v =	Channel_Circular_Velocity_Q_D_N_S(Q; D;N; S)					Velocity	v =	Channel_SemiCircular_Velocity_Q_D_N_S(Q; D; N; S)
	v =	2,713	m/s					v =	3,606	m/s

Energy	E =	Channel_Circular_Energy_Q_D_N_S(Q, D, N, S)					Energy	E =	Channel_SemiCircular_Energy_Q_D_N_S(Q; D; N; S)
	E =	0,6706	m					E =	0,9580	m

HtoD_ratio	HtoD =	Channel_Circular_H_to_D_ratio_Q_D_N_S(Q; D; N; S)					Hn to (D/2) ratio	HntoR =	Channel_SemiCircular_H_to_R_ratio_Q_D_N_S(Q; D; N; S)
	HtoD =	0,321	-					HntoR =	0,980	-

Maximum flow	Qmax =	Channel_Circular_Qmax_D_N_S					Angle or (H-R)	f or dHn =	Channel_SemiCircular_fi_dHn_Q_D_N_S			(See Note 1)
	Qmax =	2,4121	m³/s					f or dHn =	1,551	rad

Q f(HtoD) =	Q =	FlowRateForGivenHtoD_HtoD_D_N_S
	HtoD =	0,321	-				Note 1
	D =	0,92054	m				For (Hn to R) > 1, the result corresponds to the difference dHn = Hn - R [m]
	N =	0,0117	-				For Hn to R <= 1, the result corresponds to the angle f [rad]
	S =	0,011	m/m
	Q =	0,500	m³/s

Angle	f =	Channel_Circular_fi_Q_D_N_S
	f =	1,937	rad

Angle "a" for maximum flow in a circular channel
a =	0,502539401288899	rad
a = p. Case of empty circular channel
a = 0. Case of circular channel full

Critical condictions

Circular channels					Semicircular channels					Rectangular channels

Circular Channel, critical conditions (Note 1)					Semicircular Channel, critical conditions					Rectangular channel, critical conditions
Input	Q =	0,45	m3/s				Input	Q =	0,25	m3/s				Input	Q =	0,85	m3/s
	D =	0,602	m					D =	0,602	m					b =	1,4	m
	N =	0,011	-					N =	0,011	-					N =	0,011	-
	S =	0,02	m/m					S =	0,02	-

Output					Output					Output

Critical_Heigth	Hc =	Channel_Circular_Critical_Height_Q_D_N_S(Q; D;N;S)					Critical_Height	Hc =	Channel_SemiCircular_Critical_Height_Q_D_N_S					Critical_velocity	vc =	Channel_Rectangular_Critical_Velocity_Q_B
	Hc =	0,4395					Hc =	0,3244	m					vc =	1,81	m/s

Critical_Area	Ac =	Channel_Circular_Critical_Area_Q_D_N_S(Q; D;N;S)					Critical area	Ac =	Channel_SemiCircular_Critical_Area_Q_D_N_S(Q, D, N, S)					Critical_Height	Hc =	Channel_Rectangular_Critical_Height_Q_B
	Ac =	0,2227	m²					Ac =	0,1564	m²					Hc =	0,335	m

Critical_T	Tc =	Channel_Circular_Critical_Top_Width_Q_D_N_S(Q; D;N;S)					Critical_T					Critical_Energy	Ec =	Channel_Rectangular_Critical_Energy_Q_B
	Tc =	0,5345					Ec =	0,502	m

Critical_Froude	Fr_c =	Channel_Circular_Critical_Froude_Q_D(Q; D)					Critical_Froude					Critical_Froude	Frc =	Channel_Rectangular_Critical_Froude_Q_D
	Fr_c =	1					Frc =	1

Critical_P	Pc =	Channel_Circular_Critical_Wetted_Perimeter_Q_D_N_S(Q; D;N;S)					Critical_P					Hydr. Rad.	Rhc =	Channel_Rectangular_Critical_Hydraulic_Radius_Q_B
	Pc =	1,2335					Rhc =	0,2266	m

Critical_Rh	Rh_c =	Channel_Circular_Critical_Hydraulic_Radius_Q_D_N_S(Q; D;N;S)					Critical Hydraulic Rad.	Rhc =	Channel_SemiCircular_Critical_Hydraulic_Radius_Q_D_N_S					Critical slpope	Sc =	Channel_Rectangular_Critical_Slope_Q_B_N
	Rh_c =	0,1805					Rhc =	0,1576	m					Sc =	0,0029	m/m

Critical_velocity	vc =	Channel_Circular_Critical_Velocity_Q_D_N_S(Q; D;N;S)					Critical_velocity	vc =	Channel_SemiCircular_Critical_Velocity_Q_D_N_S
	vc =	2,0211					vc =	1,60	m/s

Critical_Energy	Ec =	Channel_Circular_Critical_Energy_Q_D_N_S(C7,C8,C9,C10)					Critical_Energy	Ec =	Channel_SemiCircular_Critical_Energy_Q_D_N_S
	Ec =	0,6478					Ec =	0,455	m

Critical_HtoD	HtoDc =	Channel_Circular_Critical_H_to_D_ratio_Q_D_N_S(Q; D;N;S)					Critical_HtoD
	HtoDc =	0,730

Critical angle	fc =	Channel_Circular_Critical_Angle_Q_D_N_S					Critical angle or	f_fi =	Channel_SemiCircular_Critical_fi_f_Q_D_N_S
	fc =	1,093	rad				(Hc - D/2)	f_fi =	1,493

Note1
Manning's coefficient and slope are required to ensure that
the flow rate is less than the maximum possible flow.
In the given case Qmax =		1,11	m³/s

Usually the Manning coefficient is assumed to be a constant depending only on the material.
In fact, the Manning coefficient depends on the friction factor f and on the hydraulic radius of the channel
N = (f * Rh ^ (1 / 3) / (8 * g)) ^ (1 / 2)
Where the friction factor depends on the relative rugosity Rrel and on the Reynolds number Re
f = Pipe_Friction_Factor_Rrel_Re(Rrel, Re)
with the relative rugososity is Rrel = Rabs / d
and the Reynolds number is Re = v * d / KinVisc
The hydraulic radius is Rh = A / p, thus it depends on how full the channel is.
Since the channel properties are all a function of the Manning's coefficient (among others),
the procedure will require the determination of the actual Manning's coefficient for the given application

## Index
				rev. cjc.13.06.2018

Functions. List of modules and functions (extracted)

Module E. Pipe dimensions: Carbon steel, Stainless steel, HDPE PE 100, HDPE PE80

Module H. Slurry coefficients and limit deposition velocities of slurries

Module I. Channels

E. Pipe dimensions and friction factor

For each material:		a.- Exterior diameter
		b.- Thickness
		c.- Interior diameter

E1.- Carbon steel, nominal diameter input in inches					E9.- Standard FRP pipe
E2.- Carbon steel, nominal diameter input in milimeters					E10.- Standard PVC pipes
E3.- Stainless steel, nominal diameter input in inches					E11.- Industrial PVC pipes
E4.- Stainless steel, nominal diameter input in milimeters					E12.- Pipe friction factor for Darcy-Weisbach equation
E5.- HDPE PE100, nominal diameter input in inches
E6.- HDPE PE100, nominal diameter input in milimeters
E7.- HDPE PE80, nominal diameter input in inches
E8.- HDPE PE80, nominal diameter input in milimeters

H. Slurry coefficents and limit deposition velocities

H1. McElvain & Cave correction factor

Added SaturatedWaterAbsoluteViscosity

H6.- Function for channels with normal height in meters

H7.- Function for pipes with nominal diameter in milimeters

H8.- Function for pipes with input diameter in milimeters

H9.- Function for pipes with nominal diameter in inches

H10. Limit deposition velocity for pipes, including lining

H11. Pipe_Manning-coefficient_Channels

H12. Pipe_Manning-coefficient_Pipes

I. Channels
A1. Circular channels, Normal cases			A2.- Circular channels, critical cases		B1. Semicircular channels, normal case			B2.- Semicircular channels, critical cases				C1.- Rectangular channels, normal cqases			C2.- Rectangular channels, critical cases
' A1.1.- Angle f			' A2.1.- Angle f		' B1.1.- Angle "fi" or heigth "f"			' B2.1.- Angle "fi" or heigth "f"				' C1.1.- Height			' C2.1.- Velocity
' A1.2.- Area			' A2.2.- Area		' B1.2.- Area			' B2.2.- Area				' C1.2.- Area			' C2.2.- Height
' A1.3.- Velocity			' A2.3.- Velocity		' B1.3.- Velocity			' B2.3.- Velocity				' C1.3.- Velocity			' C2.3.- Energy
' A1.4.- Height			' A2.4.- Height		' B1.4.- Height			' B2.4.- Height				' C1.4.- Energy			' C2.4.- Hydraulic radius
' A1.5.- Height to diameter ratio			' A2.5.- Height to diameter ratio		' B1.5.- Wetted perimeter			' B2.5.- Wetted perimeter				' C1.5.- Froude			' C2.5.- Critical slope
' A1.6.- Top_Width			' A2.6.- (Froude)		' B1.6.- Hydraulic radius			' B2.6.- Hydraulic radius				' C1.6.- Wetted perimeter			' C2.6.- Matrix with seven outputs
' A1.7.- Froude			' A2.7.- Top_Width		' B1.7.- Top width			' B2.7.- Top width				' C1.7.- Hydraulic radius
' A1.8.- Energy			' A2.8.- Energy		' B1.8.- Energy			' B2.8.- Energy				' C1.8.- HtoD ratio. Not applicable
' A1.9.- Wetted perimeter			' A2.9.- Wetted perimeter		' B1.9.- H to D ratio			' B2.9.- H to D ratio				' C1.9.- Top width. Not applicable T = B
' A1.10.- Hydraulic radius			' A2.10.- Hydraulic radius		' B1.10.- Froude			' B2.10.-Matrix				' C1.10.-Matrix with nine outputs
' A1.11.- Maximum flow			' A2.11.- Matrix with outputs		' B1.11.- Matrix
' A1.12.- Circular Channel_Flow at a given ratio h/d
' A1.13.- Matrix with outputs

' D1.- Circular channel with variable manning coefficient				' D2.- Semicrcular channel with variable manning coefficient				' D3.- Rectangular channels with variable manning coefficient
Output in matrix form with:				Output in matrix form with:				Output in matrix form with:
' 1.- Area "A"				' 1.- Area "A"				' 1.- Area "A"
' 2.- Hydraulic radius "Rh"				' 2.- Hydraulic radius "Rh"				' 2.- Hydraulic radius "Rh"
' 3.- Height "H"				' 3.- Height "H"				' 3.- Height "H"
' 4.- Velocity "V"				' 4.- Velocity "V"				' 4.- Velocity "V"
' 5.- Energy "E"				' 5.- Energy "E"				' 5.- Energy "E"
' 6.- Froude "Fr"				' 6.- Froude "Fr"				' 6.- Froude "Fr"
' 7.- Frition factor "F"				' 7.- Frition factor "F"				' 7.- Frition factor "F"
' 8.- Height to diameter ratio "HtoD"				' 8.- Height to diameter ratio "HtoD"				' 8.- Height to Channel_Height "HtoHchannel"
' 9.- Reynolds "Re"				' 9.- Reynolds "Re"				' 9.- Reynolds "Re"
' 10.- Manning's coefficient "N"				' 10.- Manning's coefficient "N"				' 10.- Manning's coefficient "N"
' 11.- Maximum posible flow "Qmax"				' 11.- Maximum posible flow "Qmax"				' 11.- Maximum posible flow "Qmax"
' 12.- Limit deposition velocity "Vlim"				' 12.- Limit deposition velocity "Vlim"				' 12.- Limit deposition velocity "Vlim"
' 13.- Ratio V to Vlim "VtoVL"				' 13.- Ratio V to Vlim "VtoVL"				' 13.- Ratio V to Vlim "VtoVL"
' 14.- Top width "T"				' 14.- Top width "T"				' 14.- Top width "T"
' 15.- Wetted perimeter "P"				' 15.- Wetted perimeter "P"				' 15.- Wetted perimeter "P"
' 16.- Angle fi "Fi"				' 16.- Angle fi "Fi"				' 16.-
' 17.- Outputs in matrix form "Matrix"				' 17.- Outputs in matrix form "Matrix"				' 17.- Outputs in matrix form "Matrix"

## E. Pipe dims.
				Return to Index

	E. Resume of pipe dimension functions
				9	Standard FRP pipe			Dn =	750	mm
1	Carbon steel (dn, Imperial units)			Dn =	48	in		5	HDPE PE100 (dn, Imperial units)			Dn =	24	in					PN =	Class12.5 SN5k
				SCH =	STD	-					PN =	10	bar				di =	Pipe_FRP_Dint_dn_sch =			796	mm
	di =	Pipe_Imp_CS_Dint_dn_sch		di =	1200,14	mm			di =	Pipe_Imp_HDPE100_Dint_Dn_PN		di =	555,2	mm				de =	Pipe_FRP_Dext_dn =			826	mm
	de =	Pipe_Imp_CS_Dext_dn		de =	1219,2	mm			de =	Pipe_Imp_HDPE100_Dext_Dn		de =	630	mm				s =	Pipe_FRP_Thickness_dn_sch =			15	mm
	s =	Pipe_Imp_CS_Thickness_dn_sch		s =	9,53	mm			s =	Pipe_Imp_HDPE100_Thickness_Dn_PN		s =	37,4	mm				Required Worksheet "5.FRP"

2	Carbon steel (dn, SI units)			Dn =	300	mm		6	HDPE PE100 (dn, SI units)			Dn =	1000	mm			10	Standard PVC pipes			Dn =	125	mm
				SCH =	40	-					PN =	16	bar					PN =	9
	di =	Pipe_SI_CS_Dint_dn_sch		di =	303,18	mm			di =	Pipe_SI_HDPE100_Dint_Dn_PN		di =	N/A	mm				di =	Pipe_PVC_Dint_dn_PN			42,85	mm
	de =	Pipe_SI_CS_Dext_dn		de =	323,8	mm			de =	Pipe_SI_HDPE100_Dext_Dn		de =	1000	mm				de =	Pipe_PVC_Dext_dn			48,25	mm
	s =	Pipe_SI_CS_Thickness_dn_sch		s =	10,31	mm			s =	Pipe_SI_HDPE100_Thickness_Dn_PN		s =	N/A	mm				s =	Pipe_PVC_Thickness_dn_PN			2,7	mm
				Required Worksheet "3.PVC"
3	Stainless steel (dn Imperial units)			Dn =	5	in		7	HDPE PE80 (dn, Imperial units)			Dn =	40	in
				SCH =	40S	-					PN =	6	bar			11	Industrial PVC pipes			dn =	4	in
	di =	Pipe_Imp_SS_Dint_Dn_SCH		di =	128,2	mm			di =	Pipe_Imp_HDPE80_Dint_Dn_PN		di =	886,6	mm					Sch =	80	-
	de =	Pipe_Imp_SS_Dext_Dn		de =	141,3	mm			de =	Pipe_Imp_HDPE80_Dext_Dn		de =	1000	mm				di =	Pipe_Imp_PVC_Dint_dn_sch			97,18	mm
	s =	Pipe_Imp_SS_Thickness_Dn_SCH		s =	6,55	mm			s =	Pipe_Imp_HDPE80_Thickness_Dn_PN		s =	56,7	mm				de =	Pipe_Imp_PVC_Dext_dn			114,30	mm
				s =	Pipe_Imp_PVC_Thickness_dn_sch			8,56	mm
4	Stainless steel (dn, SI units)			Dn =	150	mm		8	HDPE PE80 (dn, SI units)			Dn =	500	mm				Required Worksheet "PVC_40-80-120"
				SCH =	10S	-					PN =	16	bar
	di =	Pipe_SI_SS_Dint_dn_sch		di =	161,5	mm			di =	Pipe_SI_HDPE80_Dint_Dn_PN		di =	363,4	mm			12	Pipe friction factor for Darcy-Weisbach equation
	de =	Pipe_SI_SS_Dext_dn		de =	168,3	mm			de =	Pipe_SI_HDPE80_Dext_Dn		de =	500	mm				Relative rugosity			Rrel =	0,0004	-
	s =	Pipe_SI_SS_Thickness_dn_sch		s =	3,4	mm			s =	Pipe_SI_HDPE80_Thickness_Dn_PN		s =	68,3	mm				Reynolds number			Re =	25.000	-
				f =	0,025

Imperial			SI			Imperial			SI				HDPE PE100			HDPE 80 DIN 8074
Carbon steel pipes			Carbon steel pipes			Stainless steel			Stainless steel pipes				Imp	SI		Imp	SI			FRP			PVC industrial
dn	Sch		dn	Sch		dn	Sch		dn	Sch			dn	dn	PN	dn	dn	PN		dn	PN		dn	sch
in			mm	-		in	-		mm	-			in	mm	bar	in	mm	bar		mm	bar		in	-
1/2	5		6	STD		0,125	5S		6	5S			3/8	16	4	3/8	16	2,5		300	Class4 SN5k		0,5	40
3/4	10		8	ExStr		0,25	10S		8	10S			1/2	20	6	1/2	20	3,2		375	Class6 SN5k		0,75	80
1	20		10	XxStr		0,375	40S		10	40S			3/4	25	8	3/4	25	4		450	Class6 SN10k		1	120
1 1/2	30		15	10		0,5	80S		15	80S			1	32	10	1	32	6		525	Class10 SN5k		1,25
2	40		20	20		0,75			20				1 1/4	40	12,5	1 1/4	40	10		600	Class10 SN10k		1,5
3	60		25	30		1			25				1 1/2	50	16	1 1/2	50	16		675	Class12.5 SN5k		2
4	80		32	40		1,25			32				2	63	20	2	63			750	Class12.5 SN10k		2,5
5	100		40	60		1,5			40				2 1/2	75		2 1/2	75			900	Class16 SN10k		3
6	120		50	80		2			50				3	90		3	90			1000	Class20 SN10k		4
8	140		65	100		2,5			65				4	110		4	110			1200	Class25 SN10k		5
10	160		80	120		3			80				5	125		5	125					6
12	STD		90	140		3,5			100				5 1/2	140		5 1/2	140					8
14	XS		100	160		4			125				6	160		6	160			3.- PVC pipes			10
16	XXS		125			5			150					180			180			dn	PN		12
18			150			6			200				8	200		8	200			mm	bar		14
20			200			8			250					225			225			15	4,5		16
22			250			10			300				10	250		10	250			20	6
24			300			12			350					280			280			25	9
26			350			14			400				12	315		12	315			32	12
28			400			16			450				14	355		14	355			40	15
30			450			18			500				16	400		16	400			50	18
32			500			20			600				18	450		18	450			65
34			550			22			750				20	500		20	500			80
36			600			24					22	560		22	560			100
38			650			30					24	630		24	630			125
40			700					28	710		28	710			150
42			750					32	800		32	800			200
44			800					36	900		36	900			225
46			850					40	1000		40	1000			250
48			900					48	1200			1100			300
			1050					54	1400		48	1200			375
				64	1600		54	1400
				64	1600

## H. Slurry
				Return to Index
				www.piping-tools.net
H. Slurry coefficients					cjcruz[at]piping-tools.net
				For more information on valves, see
H1. McElvain & Cave correction factor					H5. Kinematic viscosity of a slurry					Slurry. McElvain Cave-Durand-Bingham fluids-HR value.xls

FL =	Slurry_Fl_McElvain_d50_Cv(D50, Cv)					Slurry_Visc_Thomas_Cw_Ss_RhoL_t(Cw, Ss, RhoL, t)
d50 =	900	mm				Cw =	0,28	-
Cv =	22	%				Ss =	2,8	-
FL =	1,328					RhoL =	1000	kg/m3
				t =	16	ºC
Validity:	10 mm ≤ d50 ≤ 3000 mm					KinemVisc =	1,34E-06	m²/s
	5 % ≤ Cv ≤ 40 %

Limit deposition velocity for pipes				[1]

				SI					SI		Functions with interior diameter as input				SI
H6.- Function for channels with normal height in meters					H7.- Function for pipes with nominal diameter in milimeters					H8.- Function for pipes with input diameter in milimeters
d50 =	175	mm				d50 =	250	mm				d50 =	250	mm
Cv =	25	%	5% <= Cv <= 40%			Cv =	25	%	5% <= Cv <= 40%			Cv =	25	%	5% <= Cv <= 40%
hn =	0,1	m				d =	100	mm	(Shedule STD will be used)			di =	100	mm
SS =	4,15	-				SS =	4,15	-				SS =	4,15	-
VL =	Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_hn_Ss					VL =	Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dn_Ss					VL =	Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dinterior_Ss
VL =	2,26	m/s				VL =	2,79	m/s				VL =	2,76	m/s

				Imperial					Imperial
H9.- Function for pipes with nominal diameter in inches					H10. Limit deposition velocity for pipes, including lining
d50 =	250	mm				d50 =	145	mm
Cv =	25	%	5% <= Cv <= 40%			Cv =	20,1	%
d =	4	in	(Shedule STD will be used)			dn	4	in	(Shedule STD will be used)
SS =	4,15	-				Ss =	2,65	-					www.piping-tools.net
VL =	Slurry_Limit_Deposition_Velocity_JRI_Imp_d50_Cv_dn_Ss					slining =	9	mm					Slurry_settling_velocity_according_JRI.xlsm
VL =	2,79	m/s				vL =	Slurry_Limit_Deposition_Velocity_Lining_JRI_Imp_d50_Cv_dn_Ss_Slining					cjcruz[at]piping-tools.net
				vL =	1,61	m/s

Manning's coefficient

H11. Pipe Manning's coefficient					H12. Pipe_Manning_coefficient_Pipe_d_Rabs_Re
Rh =	0,221	m				(Valid for circular pipes totally filled)
Rabs =	1,3	mm				d =	0,884	m
Re =	2,70E+06	-				Rabs =	1,3	mm
N =	Pipe_Manning_coefficient_Channel_Rh_Rabs_Re					Re =	2,70E+06	-
N =	0,0129					N =	Pipe_Manning_coefficient_pipe_d_Rabs_Re(d, Rabs, Re)
				N =	0,0129

## 5.FRP
Standard FRP Pipe Sizes (Hobas)
		WALL THICKNESS (mm)
dn [mm]	de [mm]	Class4 SN5k	Class6 SN5k	Class6 SN10k	Class10 SN5k	Class10 SN10k	Class12.5 SN5k	Class12.5 SN10k	Class16 SN10k	Class20 SN10k	Class25 SN10k		Standard FRP pipe
300	345	7	7	10	7	8	7	8	8	8	8		Application			Dn =	1200	mm
375	426	8	8	11	8	10	8	10	10	10	10		(with input validation)			PN =	Class16 SN10k
450	507	10	10	13	9	12	9	11	11	11	11		di =	Pipe_FRP_Dint_dn_sch =			1179	mm
525	587	11	11	15	11	13	11	13	13	13	13		de =	Pipe_FRP_Dext_dn =			1229	mm
600	667	13	12	17	12	15	12	15	14	14	-		s =	Pipe_FRP_Thickness_dn_sch =			25	mm
675	747	14	14	19	13	17	13	16	16	-	-
750	826	15	15	20	14	18	15	18	17	-	-
900	924	17	17	23	16	20	16	20	19	-	-
1000	1026	19	18	25	18	22	17	22	21	-	-
1200	1229	22	22	30	21	26	21	26	25	-	-

			From iPlex
NOMINAL / SIZE (DN)	OUTSIDE / DIAM.

5.- FRP pipes

FRP
dn	PN
mm	bar
300	Class4 SN5k
375	Class6 SN5k
450	Class6 SN10k
525	Class10 SN5k
600	Class10 SN10k
675	Class12.5 SN5k
750	Class12.5 SN10k
900	Class16 SN10k
1000	Class20 SN10k
1200	Class25 SN10k

## 3.PVC
15	-	-	-	-	-	1,5	1,8		Standard PVC pipes
20	26,75	-	-	-	1,5	1,9	2,2		Application			Dn =	40	mm
25	33,55	-	-	1,5	1,9	2,3	2,7		(with input validation)			PN =	12
32	42,25	-	-	1,9	2,4	2,9	3,4		di =	Pipe_PVC_Dint_dn_PN			42,85	mm
40	48,25	-	1,5	2,1	2,7	3,3	3,9		de =	Pipe_PVC_Dext_dn			48,25	mm
50	60,35	-	1,8	2,6	3,3	4,1	4,9		s =	Pipe_PVC_Thickness_dn_PN			2,7	mm
65	75,35	1,7	2,2	3,2	4,2	5,1	6,1
80	88,9	2	2,6	3,8	4,9	6,1	7,1
100	114,3	2,5	3,2	4,8	6,3	7,7	9,1
125	140,2	3	4	5,9	7,6	-	-		Application			Dn =	40	mm
150	160,3	3,4	4,5	6,7	8,8	10,8	12,8		(without input validation)			PN =	PN12
200	225,3	-	5,7	8,4	11,1	13,6	16,2		di =	Pipe_PVC_Dint_dn_PN			N/A	mm
225	250,4	4,8	6,3	9,3	12,3	15,2	18		de =	Pipe_PVC_Dext_dn			48,25	mm
250	280,4	-	7,1	10,5	13,7	17	20,1		s =	Pipe_PVC_Thickness_dn_PN			N/A	mm
300	315,5	6	8	11,7	15,5	19,1	22,6		The nominal diameter entered is wrong
375	400,5	7,7	10,1	14,9	19,6	-	-

Standard uPVC Pipe Sizes			From iPlex
NOMINAL / SIZE (DN)	OUTSIDE / DIAM.	4,5	6	9	12	15	18
		WALL THICKNESS (mm)

3.- PVC pipes
dn	PN
mm	bar
15	4,5
20	6
25	9
32	12
40	15
50	18
65
80
100
125
150
200
225
250
300
375

## PVC_40-80-120
1	2	3	4	5	6	7
2		PVC and CPVC
3		Dimensions according		ASTM D1785
4										Industrial PVC pipes
5		PVC pipe dimensions									dn =	4
6				Sch 40	Sch 80	Sch 120					Sch =	120					PVC industrial
7		NPS	de	s	s	s					dn	sch
8		in	mm	mm	mm	mm					de =	Pipe_Imp_PVC_Dext_dn					in	-
9		0,5	21,34	2,77	3,73	4,32	1,0	0,5			de =	114,30	mm					0,5	40
10		0,75	26,67	2,87	3,91	4,32	2,0	0,75					0,75	80
11		1	33,40	3,38	4,55	5,08	3,0	1			di =	Pipe_Imp_PVC_Dint_dn_sch					1	120
12		1,25	42,16	3,56	4,85	5,46	4,0	1,25			di =	92,10	mm					1,25
13		1,5	48,26	3,68	5,08	5,72	5,0	1,5					1,5
14		2	60,33	3,91	5,54	6,35	6,0	2			s =	Pipe_Imp_PVC_Thickness_dn_sch					2
15		2,5	73,03	5,16	7,01	7,62	7,0	2,5			s =	11,10	mm					2,5
16		3	88,90	5,49	7,62	8,89	8,0	3					3
17		4	114,30	6,02	8,56	11,10	9,0	4					4
18		5	141,30	6,55	9,53	NA	10,0	5					5
19		6	168,28	7,11	10,97	14,27	11,0	6					6
20		8	219,08	8,18	12,70	18,24	12,0	8					8
21		10	273,05	9,27	15,06	NA	13,0	10					10
22		12	323,85	10,31	17,45	NA	14,0	12					12
23		14	355,60	11,13	19,05	NA	15,0	14					14
24		16	406,40	12,70	21,41	NA	16,0	16					16

		Dimensions
		PVC Schedule 120 pipe shall be manufactured in strict accordance to the requirements of ASTM D1785 for physical dimensions and tolerances
		http://www.harvel.com/technical-support-center/product-specifications/pvc-pipe-schedule-120
		Schedule 120
								OD	s
		Nom. Pipe Size (in)	O.D.	Average I.D.	Min. Wall	Nom. Wt./Ft.	Max. W.P. PSI**	mm	mm
9		1/2"	0,84	0,48	0,17	0,236	1010	21,34	4,318
10		3/4"	1,05	0,69	0,17	0,311	770	26,67	4,318
11		1"	1,315	0,891	0,2	0,464	720	33,40	5,08
12		1-1/4"	1,66	1,204	0,215	0,649	600	42,16	5,461
13		1-1/2"	1,9	1,423	0,225	0,787	540	48,26	5,715
14		2"	2,375	1,845	0,25	1,111	470	60,33	6,35
15		2-1/2"	2,875	2,239	0,3	1,615	470	73,03	7,62
16		3"	3,5	2,758	0,35	2,306	440	88,90	8,89
17		4"	4,5	3,574	0,437	3,713	430	114,30	11,0998
18
19		6"	6,625	5,434	0,562	7,132	370	168,28	14,2748
20		8"	8,625	7,189	0,718	11,277	380	219,08	18,2372

										1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16
										0,5	0,75	1	1,25	1,5	2	2,5	3	4	5	6	8	10	12	14	16

										dn (in: 0.5, 0.75, 1, 1.25, 1.5, 2, 2.5, 3, 4, 5, 6, 8, 10, 12, 14, 16. Sch: 40, 80, 120

										40, 80, 120

											80
											NPS	de	s
											in	in	in
											1/2	0,84	0,147
											3/4	1,05	0,154
											1	1,315	0,179
											1 1/4	1,66	0,191
											1 1/2	1,9	0,2
											2	2,375	0,218
											2 1/2	2,875	0,276
											3	3,5	0,3
											4	4,5	0,337
											5	5,563	0,375
											6	6,625	0,432
											8	8,625	0,5
											10	10,75	0,593
											12	12,75	0,687
											14	14	0,75
											16	16	0,843

		Related Documents

		CPVC Pipes - Operating and Collapsing Pressure Ratings - Maximum operating and bursting pressures of CPVC - Chlorinated Poly(Vinyl Chloride) - piping systems
		CPVC Pipes - Support Spacing - Support spacing for CPVC pipes
		Cast Iron Soil Pipe - Cast iron soil pipe dimensions
		Comparing Friction Loss in Steel, Copper and Plastic Pipes - Water flow and friction head loss (ft/100 ft) - steel, copper and PVC plastic pipes
		PVC Pipe Schedule 40 - Friction loss and Velocity Diagram - Friction loss (psi/100 ft) and velocity for water flow in plastic PVC pipe schedule 40
		PVC Pipes - Friction Loss and Flow Velocity - Schedule 40 - Water flow in thermoplastic PVC and CPVC pipes Schedule 40 - friction loss (ft/100 ft, psi/100 ft) and flow velocities at dimensions from 1/2 inch to 16 inches
		PVC Pipes - Friction Loss and Flow Velocity - Schedule 80 - Water flow in thermoplastic PVC and CPVC pipes Schedule 80 - friction loss (ft/100 ft, psi/100 ft) and flow velocities at dimensions from 1/2 inch to 16 inches
		PVC Sewer & Drain Pipe - Dimensions of PVC sewer & drain pipes - ASTM D2729
		Pipe Formulas - Pipe and Tube Equations - moment of inertia, section modulus, traverse metal area, external pipe surface and traverse internal area - imperial units
		Plastic Pipes - Friction Head Loss - Friction head loss (ft/100 ft) in plastic pipes, PVC, PP, PE, PEH
		Plastic Pipes and Operating Pressure - ABS, PE, PVC, CPVC, PB, PP and SR
		Steel Pipes Dimensions - ANSI Schedule 40 - Internal and external diameters, areas, weights, volumes and number of threads for schedule 40 steel pipes
		Steel Pipes Dimensions - ANSI Schedule 80 - Internal and external diameters, areas, weights, volumes and number of threads for schedule 80 steel pipes
		Thermoplastic Pipes - Temperature and Maximum Support Spacing - Maximum support spacing PVC, CPVC, PVDF and PP pipes

## A1. Circular
				#NAME?
A1.- Circular channel
				Matrix output
Input					Input
	Q =	0,5	m3/s					Q =	0,5	m3/s
	D =	0,6	m					D =	0,6	m
	N =	0,011	-					N =	0,011	-
	S =	0,02	m/m					S =	0,02	m/m

Output					H =	0,2955	m
		Channel_Circular_Height_Q_D_N_S					A =	0,1387
Heigth	H =	Channel_Circular_Height_Q_D_N_S(Q, D, n, S)					T =	3,6059	m²
	H =	0,2955	m					Fr =	0,9584	-
				P =	2,3952	m
Area	A =	Channel_Circular_Area_Q_D_N_S(Q, D, n, S)					Rh =	0,9334	m
	A =	0,1387	m²					v =	0,1485	m/s
				E =	0,5999	m
TopWidth	T =	Channel_Circular_Top_Width_Q_D_N_S(Q; D; n; S)					HtoD =	0,4925	-
		0,5999					fi =	1,5859	rad
				Qmax =	1,1039	m³/s
Froude	Fr =	Channel_Circular_Froude_Q_D_N_S(Q, D, n, S)
	Fr =	2,3952	-

WettedPerimeter	P =	Channel_Circular_Wetted_Perimeter_Q_D_N_S(Q;D;n;S)
	P =	0,9334

Hydraulic radius	Rh =	Channel_Circular_Hydraulic_Radius_Q_D_N_S(Q; D; n;S)
	Rh =	0,1485	m

Velocity	v =	Channel_Circular_Velocity_Q_D_N_S(Q; D;n; S)
	v =	3,6059

Energy	E =	Channel_Circular_Energy_Q_D_N_S(Q, D, n, S)
	E =	0,9584	m

HtoD_ratio	HtoD =	Channel_Circular_H_to_D_ratio_Q_D_N_S(Q; D; n; S)
	HtoD =	0,492	-

Angle	fi =	Channel_Circular_fi_Q_D_N_S(Q, D, N, S)
	fi =	1,586	rad

Maximum flow rate	Qmax =	Channel_Circular_Qmax_D_N_S(D, N, S)
	Qmax =	1,10	m³/s

## A2. Circular Critical
A2.- Circular channel, critical conditions.
					Checking witht Hcanales					Channel_Circular_Critical_Matrix_Q_D_N_S

Input			Qmax =	Channel_Circular_Qmax_D_N_S					Q =	0,5	m3/s
Q =	0,5	m3/s	Qmax =	1,11	m³/s					D =	0,602	m
D =	0,602	m					N =	0,011	-
N =	0,011	-					S =	0,02	m/m
S =	0,02	m/m
Note. With only the two variables Q and D, the system cannot cope with all cases.					H =	0,4628	m
					A =	0,2348	m²
Output					v =	2,1296	m/s
					E =	0,6940	m
Critical_Heigth	Hc =	Channel_Circular_Critical_Height_Q_D_N_S(Q; D;N;S)					Fr =	1,0000	-
	Hc =	0,4628					P =	1,2872	m
					Rh =	0,1824	m
Critical_Area	Ac =	Channel_Circular_Critical_Area_Q_D_N_S(Q; D;N;S)					T =	0,5077	m
	Ac =	0,2348	m²					HtoD =	0,7687	-
					fi =	1,0034	rad
Critical_T	Tc =	Channel_Circular_Critical_Top_Width_Q_D_N_S(Q; D;N;S)
	Tc =	0,5077

Critical_Froude	Fr_c =	Channel_Circular_Critical_Froude_Q_D(Q; D)
	Fr_c =	1

Critical_P	Pc =	Channel_Circular_Critical_Wetted_Perimeter_Q_D_N_S(Q; D;N;S)
	Pc =	1,2872

Critical_Rh	Rh_c =	Channel_Circular_Critical_Hydraulic_Radius_Q_D_N_S(Q; D;N;S)
	Rh_c =	0,1824

Critical_velocity	vc =	Channel_Circular_Critical_Velocity_Q_D_N_S(Q; D;N;S)
	vc =	2,1296

Critical_Energy	Ec =	Channel_Circular_Critical_Energy_Q_D_N_S(C7,C8,C9,C10)
	Ec =	0,6940

Critical_HtoD	HtoDc =	Channel_Circular_Critical_H_to_D_ratio_Q_D_N_S(Q; D;N;S)
	HtoDc =	0,769

Critical angle	fc =	Channel_Circular_Critical_Angle_Q_D_N_S
	fc =	1,003	rad

					Note. Hcanales, does not give a solution for Q = 0.5 m³/s and D = 0.6 m.
					It indicates, the "H" value is greater than the diameter.
					but, the "H" value is		Hc =	0,4631	m
					and the diameter is		D =	0,6	m
					Thus, Hc < D and therefore the case has a solution

Input			Qmax =	Channel_Circular_Qmax_D_N_S
Q =	0,5	m3/s	Qmax =	1,10	m³/s
D =	0,6	m
N =	0,011	-
S =	0,02	m/m

Output

Critical_Heigth	Hc =	Channel_Circular_Critical_Height_Q_D_N_S(Q; D;N;S)
	Hc =	0,4631

Critical_Area	Ac =	Channel_Circular_Critical_Area_Q_D_N_S(Q; D;N;S)
	Ac =	0,2342	m²

Critical_T	Tc =	Channel_Circular_Critical_Top_Width_Q_D_N_S(Q; D;N;S)
	Tc =	0,5036

Critical_Froude	Fr_c =	Channel_Circular_Critical_Froude_Q_D(Q; D)
	Fr_c =	1

Critical_P	Pc =	Channel_Circular_Critical_Wetted_Perimeter_Q_D_N_S(Q; D;N;S)
	Pc =	1,2873

Critical_Rh	Rh_c =	Channel_Circular_Critical_Hydraulic_Radius_Q_D_N_S(Q; D;N;S)
	Rh_c =	0,1819

Critical_velocity	vc =	Channel_Circular_Critical_Velocity_Q_D_N_S(Q; D;N;S)
	vc =	2,1353

Critical_Energy	Ec =	Channel_Circular_Critical_Energy_Q_D_N_S(C7,C8,C9,C10)
	Ec =	0,6955

Critical_HtoD	HtoDc =	Channel_Circular_Critical_H_to_D_ratio_Q_D_N_S(Q; D;N;S)
	HtoDc =	0,772

Critical angle	fc =	Channel_Circular_Critical_Angle_Q_D_N_S
	fc =	0,996	rad

## B1. Semicircular
B1.- Semicircular channel

Input					Hcanales does not have this channel type.
	Q =	0,0068	m3/s		Case hn < R				Does, no checking with this software is possible.
	D =	0,6	m
	n =	0,0117	-
	S =	0,011	m/m

Output

Heigth	hn =	Channel_SemiCircular_Height_Q_D_N_S(Q;D; n;S)
	hn =	0,0412	m

Area	A =	Channel_SemiCircular_Area_Q_D_N_S(Q; D; n; S)
	A =	0,00847	m²		0,138492926864718

Top width	T =	Channel_SemiCircular_Top_Width_Q_D_N_S(Q; D;n; S)
	T =	0,3036	m		0,601865997022021

Froude	Fr =	Channel_SemiCircular_Froude_Q_D_N_S(Q; D; n; S)
	FR =	1,535	-		2,40335639111081

WettedPerimeter	P =	Channel_SemiCircular_Wetted_Perimeter_Q_D_N_S
	P =	0,318318377865873	m		0,932917201066913

Hydraulic radius	Rh =	Channel_SemiCircular_Hydraulic_Radius_Q_D_N_S(Q; D; n; S)
	Rh =	0,0266	m		0,148451466760752

Velocity	v =	Channel_SemiCircular_Velocity_Q_D_N_S(Q; D; n; S)
	v =	0,8030	m/s		3,61029267933955

Energy	E =	Channel_SemiCircular_Energy_Q_D_N_S(Q; D; n; S)
	E =	0,074	m		0,95920929418505

Angle fi or	fi_dHn=	Channel_SemiCircular_fi_dHn_Q_D_N_S					g =	9,80665
height dHn	fi OR dHn =	0,530530629776454	rad

	Test for a semicircular channel with hn < R					Q =	0,0068	m³s
					D =	0,6	m
	Input				Area				Height					n =	0,0117	-
	Q =	0,0068	m3/s		A = (R^2/2) * ( 2*fi - seno(2*fi) )				hn =	R - R*cos(fi)					S =	0,011	m/m
	D =	0,6	m		R =	0,3	m			R * ( 1 - cos(fi) )
	N =	0,0117	-		Fi =	0,5312	rad		R =	0,3	m					Heigth	hn =	Channel_SemiCircular_Height_Q_D_N_S
	S =	0,011	m/m		A =	0,00850	m²		fi =	0,53119	m					hn =	0,0412
					hn =	0,0413	m
					Perimeter					Area	A =	Channel_SemiCircular_Area_Q_D_N_S
	Assumed and iterated value				P =	d * fi			Top width					A =	0,0085
					d =	0,6			T =	2 * R * seno(fi)
	fi =	0,53119	rad		fi =	0,531			R =	0,3	m					Top width	T =	Channel_SemiCircular_Top_Width_Q_D_N_S
					P =	0,3187	m		fi =	0,53119	rad					T =	0,3036
	Using the function					T =	0,3039	m
	Channel_SemiCircular_fi_dHn_Q_D_N_S				Hydraulic radius					Froude	Fr =	Channel_SemiCircular_Froude_Q_D_N_S
	fi =	0,531	rad		Rh =	A / P			Velocity				E =	H + v ^ 2 / (2 * g)				Fr =	1,535
					A =	0,00850	m²		v =	Q / A			H =	0,04134	m
					P =	0,3187	m		Q =	0,0068	m³/s		v =	0,80	m/s		WettedPerimeter	P =	Channel_SemiCircular_Wetted_Perimeter_Q_D_N_S
					Rh =	0,0267	m		A =	0,0085	m²		E =	0,074	m			P =	0,318
					v =	0,8001	m/s
					Flow rate					Ratio Hn to R				Hydraulic radius	Rh =	Channel_SemiCircular_Hydraulic_Radius_Q_D_N_S
					Qcalc =	A * Rh^(2/3) * S^(1/2) * N^(-1)			Froude number				hn =	0,041	m			Rh =	0,0266
					A =	0,0085			Fr =	v / (g * (A / T)) ^ 0.5			R =	0,3	m
	Flow according Mannig´s relation				Rh =	0,0267	m		v =	0,80	m/s		hn / R =	0,14	-		Velocity	v =	Channel_SemiCircular_Velocity_Q_D_N_S
					S =	0,011	-		A =	0,0085	m²					v =	0,8030
					N =	0,0117	-		T =	0,304	m
					Qcalc =	0,0068	m³/s		Fr =	1,5279	-					Energy	E =	Channel_SemiCircular_Energy_Q_D_N_S
					This calculated flow rate Qcalc must match					E =	0,074
					the input value Q. That is obtained by iteration				Calculated flow rate
	Q = A * Rh^(2/3) * S^(1/2) * N^(-1)				with the height dHn.				Qcalc =	(S) ^ (0.5) * N ^ (-1) * (d) ^ (8 / 3) * (2) ^ (-10 / 3) * (fi - Seno(2*fi) / 2) ^ (5 / 3) * (fi) ^ (-2 / 3)					Ratio Hn to R	hn / R =	0,14
					Also, by using the VBA finction.				S =	0,011
					N =	0,012					Angle fi or dHn	fi or dHn =	Channel_SemiCircular_fiORdHn_Q_D_N_S
	g =	9,80665	m/s					d =	0,600					fi or dHn =	#NAME?
					fi	0,53119
					Qcalc =	0,0068	m³/s

					0

	Test for a semicircular channel with hn >= R					Q =	0,45	m³s
					D =	0,6	m
	Input				Semicircle (exact)				Flow rate					n =	0,0117	-
	Q =	0,45	m3/s		Asc =	(1/2)* p * R^2			Qcalc =	A * Rh^(2/3) * S^(1/2) * N^(-1)					S =	0,011	m/m
	D =	0,6	m		R =	0,3	m		A =	0,1682
	n =	0,0117	-		Asc =	0,1414	m²		Rh =	0,163012	m					Heigth	hn =	Channel_SemiCircular_Height_Q_D_N_S
	S =	0,011	m/m					S =	0,011	-					hn =	0,3447	m
					Rectangle				N =	0,0117	-
					Arectg =	dHn * D			Qcalc =	0,4500	m³/s					Area	A =	Channel_SemiCircular_Area_Q_D_N_S
	Assumed and iterated value				dHn =	0,04476	m					A =	0,1682	m²
	dHn =	0,04476	m		D =	0,6	m		This calculated flow rate Qcalc must match
					Arectg =	0,026856	m²		the input value Q. That is obtained by iteration					Top width	T =	Channel_SemiCircular_Top_Width_Q_D_N_S
	Using the function					with the height dHn.					T =	0,600	m
	dHn =Channel_SemiCircular_fiORdHn_Q_D_N_S				Total area				Also, by using the VBA function.
	dHn =	0,04473	m		A =	Asc + Arectg					Froude	Fr =	Channel_SemiCircular_Froude_Q_D_N_S
					Asc =	0,1414	m²		Height					Fr =	1,613	-
					Arectg =	0,02686	m²		hn =	R + dHn			Velocity
					A =	0,1682	m²		R =	0,3	m		v =	Q / A			WettedPerimeter	P =	Channel_SemiCircular_Wetted_Perimeter_Q_D_N_S
					dHn =	0,04476	m		Q =	0,4500	m³/s			P =	1,032	m
					Perimeter				hn =	0,34476	m		A =	0,1682	m²
					P =	p * R + 2*dHn					v =	2,67	m/s		Hydraulic radius	Rh =	Channel_SemiCircular_Hydraulic_Radius_Q_D_N_S
					R =	0,3			Top width					Rh =	0,163	m
					dHn =	0,04476			T =	0,6	m		Energy
	Flow according Mannig´s relation				P =	1,032	m					E =	H + v ^ 2 / (2 * g)			Velocity	v =	Channel_SemiCircular_Velocity_Q_D_N_S
					Froude number				H =	0,34476	m			v =	2,675	m/s
					Hydraulic radius				Fr =	v / (g * (A / T)) ^ 0.5			v =	2,67	m/s
					Dh =	2 * A / P			v =	2,67	m/s		E =	0,710	m		Energy	E =	Channel_SemiCircular_Energy_Q_D_N_S
					A =	0,1682	m²		A =	0,1682	m²					E =	0,710	m
					P =	1,032	m		T =	0,6	m		Ratio Hn to R
	Q = A * Rh^(2/3) * S^(1/2) * N^(-1)				Dh =	0,326	n		Fr =	1,613	-		hn / R =	1,15			Ratio Hn to R	hn / R =	1,15	-
					Rh =	Dh / 2
					Rh =	0,163	m					Angle fi or dHn	fi or dHn =	Channel_SemiCircular_fi_dHn_Q_D_N_S
	g =	9,80665	m/s					fi or dHn =	0,04473	m

					Channel_SemiCircular_fi_dHn_Q_D_N_S

## B2. Semicircular critical
B2.- Semicircular channel, critical condition

					Hcanales does not have this channel type.
Input					Does, no checking with this software is possible.
	Q =	0,8	m3/s
	D =	0,602	m
	N	0,011	-
	S =	0,02	m/m

Output

Critical_velocity	vc =	Channel_SemiCircular_Critical_Velocity_Q_D_N_S
	vc =	2,3534	m/s	2,12961908903025

Critical_Heigth	Hc =	Channel_SemiCircular_Critical_Height_Q_D_N_S
	Hc =	0,629	m

Critical_Energy	Ec =	Channel_SemiCircular_Critical_Energy_Q_D_N_S
	Ec =	0,912	m	0,69400150741787

Critical Hydraulic Rad.	Rhc =	Channel_SemiCircular_Critical_Hydraulic_Radius_Q_D_N_S
	Rhc =	0,21217	m	0,182400697323156

Critical area	Ac =	Channel_SemiCircular_Critical_Area_Q_D_N_S(Q, D, N, S)
	Ac =	0,3399	m²

Critical "f" or "fi"	f_fi =	Channel_SemiCircular_Critical_fi_f_Q_D_N_S
	f_fi =	0,3283

## C1. Rectangular
C1.- Rectangular channel

Input					Checking against Hcanales
	Q =	0,6	m3/s
	B =	1,4	m
	N =	0,011	-
	S =	0,02	m/m

Output

Heigth	H =	Channel_Rectangular_Height_Q_b_N_S
	H =	0,1397	m

Hydr. Rad.	Rh =	Channel_Rectangular_Hydraulic_Radius_Q_B_N_S
	Rh =	0,1165	m

Froude	Fr =	Channel_Rectangular_Froude_Q_b_n_S
	Fr =	2,620

Velocity	v =	Channel_Rectangular_Velocity_Q_b_n_S
	v =	3,07	m/s

Energy	E =	Channel_Rectangular_Energy_Q_b_n_S
	E =	0,619	m

rh =	(H * B) / (2*H + B)
H =	0,1397
B =	1,4
rh =	0,1165

## C2. Rectangular critical
C2.- Rectangular channel, critical condition
	Rectangular channel, critical conditions

Input					Checking with Hcanales
	Q =	0,6	m³/s
	B =	1,4	m

Output

Critical_velocity	vc =	Channel_Rectangular_Critical_Velocity_Q_B
	vc =	1,61	m/s

Critical_Heigth	Hc =	Channel_Rectangular_Critical_Heigth_Q_B
	Hc =	0,266	m

Critical_Energy	Ec =	Channel_Rectangular_Critical_Energy_Q_B
	Ec =	0,398	m

Critical_Froude	Frc =	Channel_Rectangular_Critical_Froude_Q_D
	Frc =	1

Hydr. Rad.	Rhc =	Channel_Rectangular_Critical_Hydraulic_Radius_Q_B
	Rhc =	0,1925	m

## Qmax
		Angle for maximum flow in a circular channel

		The flow rate can be expressed as a function
		of the diameter and the angle a as follow

							The derivatives are

							dq/da =	( (pi()-a+seno(2*a)/2)^(5/3) ) * ( (2/3) * ( pi()-a )^(-5/3) ) + ( (pi()-a)^(-2/3) ) * ( (5/3)*(pi()-a+seno(2*a)/2)^(2/3) * (-1+cos(2*a)) )

							To obtain de maximum value, the derivative shall be equal zero
							Using solver
							The dependent variable		dq/da =	-9,22290044780283E-07	(must be zero)
							The independent variable		a =	0,502539401288899	rad
							a =	28,8	º

		Input
		Q =	4,875	m3/s	Qmax =	4,9292	m3/s
		D =	1,17474	m
		N =	0,0119156	-
		S =	0,013	m/m

	For H< D/2
	Q =	D^(8/3) * 2^(-10/3) * ( Pi() - f + (1/2)*seno(2*f) )^(5/3) * (Pi() - f )^(-2/3) * S^(1/2) * N^(-1)

	f		Q		cos(fi)
	rad		m³/s
	3		0,000154		-0,989992496600445
	2,9		0,00154		-0,97095816514959
	2,8		0,0068		-0,942222340668658
	2,7		0,0201		-0,904072142017061
	2,6		0,0472		-0,856888753368947				For H > D/2
	2,5		0,0945		-0,801143615546934
	2,4		0,1691		-0,737393715541245
	2,3		0,2774		-0,666276021279824
	2,2		0,4250		-0,588501117255346
	2,1		0,6157		-0,504846104599858
	2		0,8511		-0,416146836547142
	1,9		1,1302		-0,323289566863503
	1,8		1,4491		-0,227202094693087
	1,7		1,8014		-0,128844494295525
	1,6		2,1780		-0,029199522301289
	1,5		2,5684		0,070737201667703
	1,4		2,9604		0,169967142900241				Fr =	Q*( D^2*Pi/8 + D*f)^(-3/2)* (D/g)^(1/2)
	1,3		3,3415		0,267498828624587
	1,2		3,6997		0,362357754476674
	1,1		4,0241		0,453596121425577
	1		4,3054		0,54030230586814
	0,9		4,5371		0,621609968270664
	0,8		4,7149		0,696706709347165
	0,7		4,8380		0,764842187284488
	0,6		4,9079		0,825335614909678
	0,59		4,9122		0,830940679100164
	0,58		4,9159		0,836462649915187
	0,57		4,9192		0,841900975162269
	0,56		4,9220		0,847255111013416
	0,55		4,9243		0,852524522059506
	0,54		4,9262		0,857708681363824
	0,53		4,9276		0,862807070514761
	0,52		4,9286		0,86781917967765
	0,51		4,92909		0,872744507645751
fiQmax =	0,502539401288899	Qmax =	4,929	(HtoD)Qmax =	0,876
	0,5		4,92920		0,877582561890373
	0,4		4,9083		0,921060994002885
	0,3		4,8535		0,955336489125606
	0,21953288493999		4,791	HtoD =	0,976
	0,2		4,7743		0,980066577841242
	0,1		4,6805		0,995004165278026
	0		4,5823		1
	f		Q		cos(fi)
	rad		m³/s

## Q(HtoD)
				#NAME?

	Flow rate in a circular channel for a
	given ratio HtoD					Data					Using the function
				Ratio H to D		HtoD =	0,321	-		HtoD =	0,321	-
	HtoD =	H / D					Circle diameter		D =	0,92054	m		D =	0,921	m
				Manning's coefficient		N =	0,0117	-		N =	0,0117	-
				Slope		S =	0,011	m/m		S =	0,011	m/m
				Q =	FlowRateForGivenHtoD_HtoD_D_N_S
				Angle "f"					Q =	0,500	m³/s
				f =	acos(2*HtoD - 1)
				HtoD =	0,321
				f =	1,937	rad

				Flow rate
				Q = D^(8/3) 2^(-10/3)*( p-f +(1/2) *seno(2*f) )^(5/3) * (p-f)^(-2/3) S^(1/2)*N^(-1)
				D =	0,92054	m
				f =	1,9371	rad
				N =	0,0117	-
				S =	0,0110	-
				Q =	0,500	m³/s

				Checking of "HtoD" for the calculated flow rate using the function
				Hto D = Channel_Circular_H_to_D_ratio_Q_D_N_S
				Q =	0,500	m³/s
				D =	0,92054	m
				N =	0,0117	-
				S =	0,011	m/m
				HtoD =	0,321	-

	For equation deductions, see Annex Equations, below

				#NAME?
Annex Equations

## Deductions
	Deduction of equations for channels

						1

	A.- Circular channels				C.-Rectangular channels

	A1.- Circular channels, normal case				C1.- Rectangular channels, normal case

	A2.- Circular channels, critical case				C2.- Rectangular channels, critical case

					Qmax
	B.- Semicircular channels
					Q(HtoD)
	B1.- Semicircular channels, normal case
					Deductions
	B2.- Semicircular channels, critical case
					Equations

						2
	A.- Circular channels

	A1.- Circular channels, normal case

	Geometrical relations for circular channels
	1.- Flow area, for a given angle f			Eq. (a)
	2.- Wetted perimeter			Eq. (b)
	3.- Hydraulic radius			Eq. (c)

	Volume flow rate
	4.- Flow according Mannig´s relation			Eq. (d)

	Other channel properties
	5.- Heigth
	6.- Heigth to diameter ratio
	7.- Top Width
	8.- Velocity
	9.- Energy
	10.- Froude

						3
	A1.- Circular channels, normal case

	This deductions correspond to an angle f as defined in the Figure A.

	1.- Flow area, for a given angle f in a circular channel

						2.- Wetted perimeter

						3.- Hydraulic radius

						4
4.- Flow according Mannig´s relation						Application

						Q =	0,4	m3/s
			(d)			Q = A * Rh^(2/3) * S^(1/2) * N^(-1)			(d)			D =	0,92054	m
						N =	0,0117	-
						S =	0,011	m/m

						f =	Channel_Circular_fi_Q_D_N_S
						f =	2,013	rad

						Q =	D^(8/3) * 2^(-10/3) * ( (p-f ) + (1/2)*sin(2*f ))^(5/3) * ( p-f )^(-2/3) * S^(1/2) * N^(-1)
						D =	0,92054	m
						f =	2,01322	rad
						S =	0,011	m/m
						N =	0,0117	-
	Q =	D^(8/3) * 2^(-10/3) * ( (p-f ) + (1/2)*sin(2*f ))^(5/3) * ( p-f )^(-2/3) * S^(1/2) * N^(-1)					(d1)
						Q =	0,40	m3/s

	Relation applied in the code

	Q =	(S)^(0.5) * n^(-1) * (D)^(8/3) * (2)^(-10 / 3) * (Pi - fi + Sin(2*fi) / 2)^(5/3) * (Pi - fi)^(-2/3)					(d2)
						Using equation (d2)

						Q =	(S)^(0.5) * n^(-1) * (D)^(8/3) * (2)^(-10 / 3) * (Pi - fi + Sin(2*fi) / 2)^(5/3) * (Pi - fi)^(-2/3)
						S =	0,011	m/m
						5		N =	0,0117	-
	Circular flow relationships					D =	0,92054	m
						f =	2,01322	rad
1	Flow area					6	Heigth to diameter ratio					Q =	0,40	m3/s
	A = (D / 2) ^ 2 * (pi - fi + (1 / 2) * Sin(2 * fi))			(a)			H/D = (1 / 2) * (1 + Cos(fi))

2	Wetted perimeter					7	Top Width
	P = D * (pi - fi)			(b)			(from Fig. A)
						T = 2 * (D / 2) * Sin(fi)
3	Hydraulic radius
	Rh = A / p			(c)		8	Velocity
						v = Q/A
4	Flow rate
						9	Energy
	Q = A * Rh^(2/3) * S^(1/2) * N^(-1)			(d)			E = H + v^2/(2*g)

						10	Froude
						(see sheet Froude)
						Fr = v / (g * hdepth) ^ 0.5
	Q = (S)^(0.5) * n^(-1) * (D)^(8/3) * (2)^(-10 / 3) * (Pi - fi + Sin(2*fi) / 2)^(5/3) * (Pi - fi)^(-2/3)					Fr = v / (g * (A / T)) ^ 0.5
					(d2)
5	Heigth
	(from Fig. A)
	H = (D / 2) * (1 + Cos(fi))

						6
	A2.- Critical flow in circular channels

	The Froude number is defined as

					Fr^2 =	(64/g) * (Q^2/D^5) * sin(f) / (pi()-f+(1/2*sin(2*f)))^3

				Fr =	[ (64/g) * (Q^2/d^5) * sin(f) / (pi()-f+(1/2*sin(2*f)))^3 ]^0.5					(e)

				Using equation (e) the angle f for the ocurrence of critical conditions is determined: Fr = 1
				Then, the other properties can be determined.

						7
	B1.- Semicircular channels, normal case

	Semi-circular flow relationships (for H>D/2)
	(Figure C)

	For H <= D/2, the relations for circular
	channels are valid

1	Flow area
	A = (1 / 2) * (Pi() * D ^ 2 / 4) + D * f

2	Wetted perimeter
	P=pi()*d/2 + 2*f

3	Hydraulic radius			7	Top width		Hydraulic depth
	Rh =( pi()*d^2 + 8* d * f) / (4 * pi() * d + 16 * f ) )				T = D		hdepth = A / T

4	Flow rate			8	Velocity	10	Froude number
	Q = A * Rh^(2/3) * S^(1/2) * N^(-1)				v = Q / A		(see sheet Froude)
	(replacing equations 1 and 3 in Manning's eq.)					Fr = v / (g * hdepth) ^ 0.5
				9	Energy		Fr = v / (g * (A / T)) ^ 0.5
5	Heigth				E = H + v^2/(2*g)
	H = (D / 2) + f

6	Height to Diameter ratio
	HtoD_ratio = H / D

						8
	B2.- Semicircular channels,critical case
					If H > D/2

				Fr^2 =	(Q^2/g)*( D^2*p/8 + D*f)^(-3)*D

				'Fr = Q * (D ^ 2 * Pi / 8 + D * f) ^ (-3 / 2) * (D / g) ^ (1 / 2)					(f)

				Using equation (f) the angle f for the ocurrence of critical conditions is determined: Fr = 1
				Then, the other properties can be determined.
	If H< D/2
	For H <= D/2, the same
	relations as for a circular
	channel are valid.

					Rectangular channel, critical condition					9
	C1.- Rectangular channels, normal case

The height "h" is found by iteration using Manning's equation

Manning						For the critical case		with
v =	(1/n) * R^(2/3) * S^(1/2)
v =	(1/n) * ((b*h)/(b+2*h))^(2/3) * S^(1/2)
v =	Q / ( b * h)

Q / ( b * h) =	(1/n) * ((b*h)/(b+2*h))^(2/3) * S^(1/2)
Q =	(1/n) * ((b*h)/(b+2*h))^(2/3) * S^(1/2) * (b*h)

A =	b * h
v =	Q / A		Critical slope
v =	Q / ( b * h)		If Fr = 1

P =	b + 2*h
R =	A / P
R =	(b*h) / (b+2*h)

Froude

						10

	Qmax =	( B * Hchannel* ( HtoHchannel )max )^(5/3) * ( 2*Hchannel * ( HtoHchannel )max + B )^(-2/3) * S^(1/2) * N^(-1)

	B =	0,5	m
	Hchannel =	1	m		H =	Hchannel * (HtoHchannel)max
	(HtoHchannel)max =	0,6	-		Hchannel =	1	m
	S =	0,01	m/m		(HtoHchannel)max =	0,6	-
	N =	0,011	-		H =	0,6	m
	Qmax =	0,858	m³/s
					P =	2*H + B
					H =	0,6	m
	v =	R^(2/3) * S^(1/2) * N^(-1)			B =	0,5	m
	R =	0,176	m		P =	1,7	m
	S =	0,01	m/m
	N =	0,011	-		A =	B * H
	v =	2,86	m/s		B =	0,5	m
					H =	0,6	m
	Q =	A * v			A =	0,3	m²
	A =	0,3	m/s
	v =	2,86	m/s		R =	A / P
	Q =	0,858	m³/s		A =	0,3	m²
					P =	1,7	m
					R =	0,176	m

## Equations
Equations

Eq. 1					Eq. 7		(Note 1)			Eq. 13		(Note 2)		Note 1
Design volume flow rate, with froth					Viscosity of slurry					Dynamic viscosity ratio of slurry				For heterogeneous slurries,
QD,F =	(ms /( rP *Cw )) * FF * DF				nP =	Slurry_Visc_Thomas_Cw_Ss_RhoL_t				mp/mL =	(1+2.5*Cv+ 10.05*Cv^2 + 0.00273* exp(16.6*Cv))			Newtonian rheology.
					Thomas, 1965. (Slurry systems
Eq. 2					Eq.8					Eq. 14				handbook [4])
Maximum volume flow rate, with froth					Pulp mass flow rate					Water dynamic viscosity				Equation 1-9 is widely accepted
Qmax =	Qnom * Qmax / Qnom * FF * DF				mP =	ms / Cw				mL =	SaturatedWaterAbsoluteViscosity_t			in the slurry industry for
					heterogeneous mixtures of a
Eq. 3					Eq. 9					Eq. 15				Newtonian rheology.
Minimum volume flow rate, with froth					Pulp volume flow rate					Pulp dynamic viscosity
Qmin =	Qnom * Qmin / Qnom * FF * DF				Qp =	mp / rp				mp =	mp/mL * mL			Note 2
					Validity	0 % <=Cv <= 65%
Eq. 4					Eq. 10					Eq. 16
Specific gravity of solids					CS pipe exterior diameter					Pulp kinematic viscosity
Ss =	rs / rL				de =	Pipe_Imp_CS_Dext_dn				np =	mp / rp

Eq. 5					Eq. 11					Eq. 17
Pulp density					CS pipe thickness					Limit deposition velocity
rP =	(rL*Ss)/(Cw+(1-Cw)*Ss)				s =	Pipe_Imp_CS_Thickness_dn_sch				vd =Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_D_Ss

Eq. 6					Eq. 12					Eq. 18
Volumetric concentration					Lined pipe interior diameter					Kinematic pressure
Cv =	100 *				di =	de - 2 * (s +sLining)				hkinem =	v^2 / (2*g)

Eq. 19					Eq. 25		[m]				Eq. 31
Relative rugosity		[-]				Normal height (depth)					Froude number		[-]
Rrel =	Rabs / Di					hn = Channel_Circular_Height_Q_D_N_S					Fr = Channel_Circular_Froude_Q_D_N_S

Eq. 20					Eq. 26					Eq. 32
Reynolds number					Wetted area		[m²]				Velocity ratio
Re =	v * Di / n					A = Channel_Circular_Area_Q_D_N_S					v/vd =	v / vd

Eq. 21					Eq. 27					Eq. 33
Friction factor		[-]				H to D ratio		[-]				Maximum flow		[m³/s]
f = Pipe_Friction_Factor_Rrel_Re					HtoD=Channel_Circular_H_to_D_ratio_Q_D_N_S					Qmax = Channel_Circular_Qmax_D_N_S

Eq. 22					Eq. 28
Mc Elvain & Cave correct. factor					Hydraulic radius		[m]
FL = Slurry_Fl_McElvain_d50_Cv					Rh=Channel_Circular_Hydraulic_Radius_Q_D_N_S

Eq. 23					Eq. 29
Manning's coefficient_Channel					Velocity		[m/s]
N = Pipe_Manning_coefficient_Channel_Rh_Rabs_Re					v = Channel_Circular_Velocity_Q_D_N_S

Eq. 24					Eq. 30
Manning's coefficient_Circular pipe, full					Energy		[m]
N =	( ( f * d^(1/3) ) / ( 2^(11/3) *g) )^0.5					E = Channel_Circular_Energy_Q_D_N_S

## Ref
References

www.piping-tools.net
Carlos J. Cruz
cjcruz[at]piping-tools.net