## Index
				Rev. cjc. 01.08.2018

	Expansion loop calculation

	Index

1	Expansion loop (CS)	Routine for the expansion loop calculation for a CS pipe

2	Deduction	Deduction of the expansion loop equation

3	Table A-1.	Allowable stress for the material as functiuon of temperature

4	Lambda.	Coefficient of linear expansion of some of the most common materials.

5	Elasticity module	Elasticity modules of materials at different temperatures

6	Spiraxsarco.	Spiraxsarco Chart for expansion loops sizing

7	Vitaulic.	Victaulic equation for expansion loops sizing

8	Properties	Phisical properties of some materials

9	U.S. Army Corps	U.S. Army Corps of Engineers

	References					www.piping-tools.net
				Expansion_loop.xlsm
				cjcruz[at]piping-tools.net

## 1b.- for PVC pipe
				Rev. cjc. 03.04.2016

Example of an Expansion loop for a PVC pipe
				H = / =

Material:	PVC 80			Exterior pipe diameter				Length "L" of expansion loop
Pipe length at installation temperature				de =	Pipe_Imp_PVC_80_Dext_dn
Linst =	40,0	m		dn =	10	in
Installation temperature				de =	273,05	mm
tinst =	10	ºC		de =	0,2731	m
Maimum pipe temperature					Expansion loop of PVC schedule 80
tmax =	35	1C		Temperature difference
PVC nominal pipe diameter				Dt =	tmax - tinst			Length "L" of expansion loop
dn =	10	in		tmax =	35	ºC		L =	0.378 * ( (3 * E * d * DL) / (sadm) )^0.5
Linear expansion coefficient of PVC				tinst =	10	ºC		E =	3,0E+09	Pa
From sheet 8				Dt =	25	K		de =	0,273	m
l =	5,04E-05	m / (ºC*m)					DL =	0,050	m
Modulus of elasticity @ 23 ºC				Pipe expansion				sallow =	5,52E+07	Pa
From sheet 8				DL =	Linst * l * Dt			L =	0,6	m
E =	3,0E+09	Pa		Linst =	40,0	m		W =	0,3	m
Tensile strength @ 23 ºC				l =	5,04E-05	m / (ºC * m)
s =	5,52E+07	Pa		Dt =	25,0	ºC
				DL =	0,050	m

	PVC

Annexes A, B y C
Anexo A					Se asume que el punto "A" corresponde
Interpolación para el esfuerzo admisible del material					(Tabla A-1, Hoja 3)				al caso de una viga empotrada en cuyo
				extremo "C" se produce una deflección
t =	#REF!	°C	(Para t < 38 °C, la tabla utiliza 38 °C)					DL/2. Para deflexión máxima de la viga,
Row =	API 5L - Gr. B	(Selected material)					se quiere que ésta no sufra un esfuerzo
				superior a sallow.
Col_A =	#REF!	tA =	#REF!	°C	sA =	#REF!	MPa
Col_B =	#REF!	tB =	#REF!	°C	sB =	#REF!	MPa		Tipo de lira
				L =	2 * W
S =	sB + (sA - sB) * (tb - t)/(tb - ta)
S =	#REF!	MPa	0	Temperature out of range

Anexo B
Interpolación para el módulo de elasticidad del tipo de material					(Tabla B, Hoja 5)
			Para t < -200 °C, se usan datos para -200 °C
t =	Err:508	°C	Información disponible, para la mayoría de los tipos de materiales, tmax = 649 °C.
Row =	1	(Selected material)
				MPa
Col_A =	Err:508	tA =	Err:508	°C	EA =	Err:508
Col_B =	Err:508	tB =	Err:508	°C	EB =	Err:508	MPa

E =	EB + (EA - EB) * (tb - t)/(tb - ta)
E =	Err:508	MPa	0	Temperature out of range for selected material

Anexo C
Interpolación para el coeficiente de expansión térmica del material					(Tabla C, Hoja 4)

t =	#REF!	°C	(Para t < 38 °C, la tabla utiliza 38 °C)
Row =	25Cr-20Ni	(Selected material)

Col_A =	#REF!	tA =	#REF!	°C	lA =	#REF!	m/(m*K)
Col_B =	#REF!	tB =	#REF!	°C	lB =	#REF!	m/(m*K)

l =	sB + (sA - sB) * (tb - t)/(tb - ta)
l =	#REF!	m/(m*K)	0	Temperature out of range for selected material
Do not delete these lines

Carbon steel pipes

Carbon steel pipes
dn	Sch
in	-
1/2	5
1	10
1	20
2	30
2	40
3	60
4	80
5	100
6	120
8	140
10	160
12	STD
14	XS
16	XXS
18
20
22
24
26
28
30
32
34
36
38
40
42
44
46
48

## 2.- Deduction (sp)
				Rev. cjc. 01.08.2018

Cálculo de lira considerando la flexión en los dos brazos y el giro en los codos					1 de 4

El cálculo de la longitud "L" de los brazos se realiza considerando la condición de que se produzca como máximo un esfuerzo de flexión admisible "sadm"
				f		f
El aumento de temperatura produce una extensión de DLinst en la cañería
		Lira					C		DC

				b / L
La dilatación de la cañería produce una deflexión "DLinst/2"
en el punto "C" del a brazo izquierdo "AC" de la lira.
Lo mismo ocurre en el brazo "BD" de la lira.
				A		B
En los extremos "C" y "D" de la lira se produce una flecha					L/2
f = DLinst/2

Esta flecha se debe en parte a una flexión de los brazos
y en parte al giro en los codos en "A" y "B".
Estas dos flechas se deben a la fuerza "P" originada por
la extensión de la cañería. Esta fuerza produce una flecha
"f1" debida a la flexión del brazo y una flecha "f2" debida
al giro del codo.

				2 de 4
Viga en voladizo con carga concentrada				Una flecha "f2", debida al giro del codo				Ecuación diferencial de la curva				Para x = m/2
en el extremo libre (brazos)				de la lira en el punto "A", se agrega a				deformada de la viga "A-B" (Figura 2)				dy/dx =	0
f1 / L / P				la flecha "f1" debida a la flexión del
				brazo. La flecha total es		f = f1 + f2					luego
A				f / A / L / m / Lira / B / P / x / y / a / C / DC
		C					con
				(3)		Reemplazando en (3)

				se tiene
	Figura 1

Flecha. [1]. Tabla 8.1, página 218
Flecha debida a la flexión de la viga					Intergrando

		(1)

Fuerza "P" asociada a la flecha f1					Figura 2					(4)

		(2)		La viga A-B se deforma por momentos
				aplicados en sus dos extremos

				3 de 4
La pendiente es				luego,				y la flecha en el punto C debida al				Relaciones f/f1 y f/f2
				giro en el codo A es

				(5)
Pendiente en el codo A (en x = 0)				Para el brazo L , la flecha f2
				debida al giro del codo es				La flecha total en C es

				luego

Definiendo una razón largo/brazo
L/m =	2
m =	L/2					(4)

				La flecha en el punto C debida a la
				flexión del largo "L" de la lira es

				(1)

				4 de 4
Esfuerzo máximo				Reemplazando f1				Para la lira completa, es decir
				considerando la deflexión de los dos
		(5)			(1)			brazos, se tiene que

con c = d/2

		(6)

de (3)					Esta es la longitud del brazo de la
				lira que, para la expansión dada de
				la cañería, produce el esfuerzo
y reemplazando P de (2)				Despejando					máximo admisible "smax"
				Ver Hoja Vitaulic. Vitaulic propone
				misma ecuación, con la diferencia
				que el factor 0.378 es redondeado
				a 0.4 (Hoja 7)

				(7)

				Relación válida para la deflexión
				de un brazo

Momento en el codo (punto A)

Reemplazando la fuerza P por (2)
		(2)

Para una viga en cantilever "AC",
el momento inducido en "A" por
una flecha impuesta en el punto "C,
debida a la dilatación de la cañería,
es

## 1. Expansion loop
				Rev. cjc. 01.08.2018
				Note 1. The pipe dimensions are automatically calculated only
Expansion loop for a steel pipe					Heigth "H" of expansion loop					for carbon steel materials ccording ANSI B36.10M.
Steel pipe expansion loop with nominal diameter "dn" shedule "SCH" and length "Linst"					For other materials, the interior and exterior diameter
The given length "Linst" refers to an installation at a temperature "tinst".					dimensions must be entered manually into the corresponding cells
The pipe will expand with respect to its length "Linst", due to the temperature rise Dt = tmax - tinst
The maximum temperature could be reached due to the ambient temperature and solar radiation,
or due to fluid flowing through it.
Similarly, the pipe could shrink due to low ambient temperatures and radiation to the sky.

Data
Material:
dn =	10	in		Elasticity module
SCH =	40			Elasticity module of selected material
Linst =	100	m		at operation temperature (Annex B)
tinst =	10	ºC		Material type, to obtain "E"
toperation =	174,2	°C
				E =	1,93E+11	Pa
Allowable stress					Temperature differential				Pipe expansion DL				Carbon steel expansion loop
Allowable stress of selected material				Auxiliary data				Dt =	toperation - tinst			The expansion loop will absorb this				Heigth "H" of expansion loop
at operation temperature				Pipe dimensions (Note 1)				toperation =	174,2	ºC		length				H = 0.378*( (3 * E * de * DL) / (sallow) )^0.5
sallow =	137,9	MPa		dn =	10	in		tinst =	10	ºC		DL =	l * Linst * Dt			E =	1,93E+11	Pa
Linear expansion coefficient				SCH =	40	-		Dt =	164,2	K		l =	1,61E-05	m/(m*K)		de =	0,273	m
Expansion coefficient of selected				di =	Pipe_Imp_CS_Dint_dn_sch					Linst =	100	m		DL =	0,264	m
material at operation temp. (Annex C)				di =	254,46	mm					Dt =	164,2	K		sallow =	1,379E+08	Pa
Mat. type				de =	Pipe_Imp_CS_Dext_dn					DL =	0,26	m		H =	6,6	m					www.piping-tools.net
l =	1,61E-05	m/(m*K)		de =	273	mm					DL =	264,19	mm		W =	3,3	m					Expansion_loop.xlsm

				Annexes A, B y C

Annex A					f / A / H / m / Lira / B / P / x / y / a / C / DC
Interpolation for permissible material stress					(Table A-1, Sheet 3)					Expansion loop dimensions ratio
				H / w =	2
t =	174,2	°C		(For t < 38 °C, the table uses 38 °C)
Row =	9	(Cell associated with selected material from table A-1)					It is assumed that the point A coresponds
				to the fxed end of a cantilever beam AC.
Col_A =	5	tA =		148,9	°C	sA =		137,9	MPa
Col_B =	6	tB =		204,4	°C	sB =		137,9	MPa			At the point C of this beam a deflection f = DL/2
				is produced, due to force P. This force P is
S =	sB + (sA - sB) * (tb - t)/(tb - ta)					caused by the temperature change acting on
S =	137,9	MPa		1					the pipe.
				The beam AB deforms due to the application
Annex B					of the moment P*H at his end A.
Interpolation for the modulus of elasticity of the material type					(Table B, Sheet 5)					As a result of the application of this moment
				For t < -200 °C, one uses data for t = -200 °C					a rotation a occurs at end of the beam.
t =	174,2	°C		Information available, for most types of materials, tmax = 649 ° C.
Row =	1	(Cell associated with selected material from table B)

Col_A =	7	tA =		149,0	°C	EA =		2,0E+11	MPa
Col_B =	8	tB =		204,0	°C	EB =		1,9E+11	MPa

E =	EB + (EA - EB) * (tb - t)/(tb - ta)
E =	1,9E+11	MPa		1

Annex C
Interpolation for the coefficient of thermal expansion of the material					(Table C, Sheet 4)

t =	38	°C		(For t < 38 °C, the table uses 38 °C)
Row =	5	(Cell associated with selected material from table C)

Col_A =	43	tA =		33,9	°C	lA =		1,6E-05	m/(m*K)
Col_B =	44	tB =		47,8	°C	lB =		1,6E-05	m/(m*K)

l =	sB + (sA - sB) * (tb - t)/(tb - ta)
l =	1,61E-05	m/(m*K)		1

Do not delete these lines

Carbon steel pipes

Carbon steel pipes
dn	Sch
in	-
1/2	5
1	10
1	20
2	30
2	40
3	60
4	80
5	100
6	120
8	140
10	160
12	STD
14	XS
16	XXS
18
20
22
24
26
28
30
32
34
36
38
40
42
44
46
48

## 2. Deduction
				Rev. cjc. 01.08.2018
				1 of 4
Expansion joint calculation considering the arms bending and the rotation of the elbows

The calculation of the heigth "H" of the arms is done considering the requirement of a maximum allowable bending stress "sallow"

Expansion joint / L
				A / B / C / D / H / W / f / f

The temperature rise produces an extension of the pipe length.
Dilation of the pipe produces a deflection "DL / 2"
in the point "C" of the left arm "AC". The same occurs in the
arm BD.

The expansion joint shall absorb the total dilation DL
without surpassing the given maximum material stress.

Each half of the expansion joint shall permit a displacement
f = DL / 2. This shift f will be produced by the contribution of:
1) Flexion of arm AC, denoted as f1
b) Displacement of point C due to the rotation of the elbow in A, denoted as f2

				2 of 4
				A deflection "f2", due to rotation of the				Differential equation for the beam AB				For x = w/2	(midelpoint)
Analysis for a half of the expansion loop				elbow of the expansion joint in point "A"				(Figure 2)				dy/dx =	0
				is added to arrow "f1" due to bending
				of arm.					thus
Cantilever beam with concentrated load				The total deflection is		f = f1 + f2
				with
f1 / H / P				f / A / H / w / Lira / B / P / x / y / a / C / DC					(3)		Replacing in (4)

A
		C

				(4a)
				Integrating
	Figure 1
Deflextion. Ref. 7. Figure 13
Cantilever beam, concentrated load
at free end
				(4)
		(1)
				Figure 2
				The beam AB deforms due to the
Force "P" associated with the deflextion				moments applied at both ends

		(2)

				3 of 4
The slope is Eq. (4a)				Thus,				From equation (1), the deflextion of				Relations f/f1 y f/f2
				point C due to the flexión of arm AC
				is

Slope at the elbow B (in x = w)				The tangent of the angle due to the					(1)
				rotation of the elbow is
				and the deflextion of point C due to
				the rotation of the elbow in A es

				thus					(4b)

				The total delextion in C is
Defining a ratio Higth to Width
H/w =	2
w =	H/2					(4b)

				(4c)

				4 of 4
Maximum stress in beam AC				Reaplacing f1				For the complete expansion joint
(From the moment being applied
to beam AB)					(1)

		(5)					This is the length H of the expansion
				joint that, for the given conditions,
with c = d/2					will have as a result the maximum
				permissible "smax".
		(6)
				See Sheet Victaulic. Victaulic
from (3)				One obtains					indicates the same equation, with
				the difference that the factor 0.378
		(3)					is rounded to 0.4 (Sheet 7).
and replacing P from (2)

		2
				(7)

				Valid for one half expansion joint

## 3. Table A-1
			Table A-1

	9		Allowable stress as function of temperature [MPa]
	API 5L - Gr. B		TEMPERATURE °C
	1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20	21	22	23	24	25	26
	Spec & Grade	Material	38	93	149	204	260	316	343	371	399	427	454	482	510	538	566	593	621	649	677	704	732	760	788	816
	1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20	21	22	23	24	25	26
1	A 53(Type F) Gr.A	1	110,3	110,3	110,3	110,3	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"
2	A 53 - Gr. A	2	110,3	110,3	110,3	110,3	110,3	102,0	100,0	99,3	73,8	64,1	54,5	44,8	31,0	17,2	11,0	6,9	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
3	A 53 - Gr. B	3	137,9	137,9	137,9	137,9	130,3	119,3	117,2	113,8	89,6	74,5	60,0	44,8	31,0	17,2	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
4	A 106 - Gr. A	4	110,3	110,3	110,3	110,3	110,3	102,0	100,0	99,3	73,8	64,1	54,5	44,8	31,0	17,2	11,0	6,9	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
5	A106 - Gr. B	5	137,9	137,9	137,9	137,9	130,3	119,3	117,2	113,8	89,6	74,5	60,0	44,8	31,0	17,2	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
6	A106 - Gr. C	6	160,6	160,6	160,6	157,9	148,9	135,8	133,8	132,4	102,0	82,7	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
7	API 5L - Gr. A	7	110,3	110,3	110,3	110,3	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
8	API 5L - Gr. A25	8	103,4	103,4	100,0	95,1	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
9	API 5L - Gr. B	9	137,9	137,9	137,9	137,9	130,3	119,3	117,2	113,8	89,6	74,5	60,0	44,8	31,0	17,2	11,0	6,9	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
10	API 5L - Gr. X42	10	137,9	137,9	137,9	137,9	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
11	API 5L - Gr. X46	11	144,8	144,8	144,8	144,8	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
12	API 5L - Gr. X52	12	151,7	151,7	151,7	151,7	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
13	API 5L - Gr. X56	13	163,4	163,4	163,4	163,4	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
14	API 5L - Gr. X60	14	172,4	172,4	172,4	172,4	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
15	API 5L - Gr. X65	15	177,2	177,2	177,2	177,2	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
16	API 5L - Gr. X70	16	188,2	188,2	188,2	188,2	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
17	API 5L - Gr. X80	17	206,8	206,8	206,8	206,8	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"NA"	"N/A"
18	A312 - Gr. TP 304	18	137,9	137,9	137,9	128,9	120,7	113,1	111,7	110,3	107,6	104,8	102,7	100,7	99,3	95,1	84,1	66,9	53,1	41,4	32,4	25,5	20,0	15,9	12,4	9,7
19	A312 - Gr. TP 304L	19	115,1	115,1	115,1	108,9	102,0	96,5	94,5	93,1	91,7	89,6	88,3	82,0	68,3	53,8	43,4	35,2	27,6	22,1	17,9	14,5	11,7	7,6	6,9	6,2
20	A312 - Gr. TP 304H	20	137,9	137,9	137,9	128,9	120,7	113,1	111,7	110,3	107,6	104,8	102,7	100,7	99,3	95,1	84,1	66,9	53,1	41,4	32,4	25,5	20,0	15,9	12,4	9,7
21	A312 - Gr. TP 309	21	137,9	137,9	137,9	137,9	137,9	132,4	129,6	126,2	124,1	120,7	100,7	95,8	86,2	72,4	58,6	44,8	34,5	26,2	20,0	15,9	12,4	9,0	6,2	4,8
22	A312 - Gr. TP 310	22	137,9	137,9	137,9	137,9	137,9	132,4	129,6	126,2	124,1	120,7	100,7	95,8	86,2	75,8	49,0	34,5	24,8	17,2	10,3	5,5	3,4	2,8	2,1	1,4
23	A312 - Gr. TP 316	23	137,9	137,9	137,9	133,1	123,4	117,2	115,1	112,4	111,0	109,6	108,2	106,9	106,2	105,5	100,0	85,5	67,6	51,0	37,9	28,3	21,4	15,9	11,7	9,0
24	A312 - Gr. TP 316L	24	115,1	115,1	115,1	106,9	99,3	93,1	91,0	88,9	86,9	85,5	83,4	81,4	79,3	77,2	74,5	70,3	60,7	44,1	32,4	24,1	17,2	12,4	9,0	6,9
25	A312 - Gr. TP 316H	25	137,9	137,9	137,9	133,1	123,4	117,2	115,1	112,4	111,0	109,6	108,2	106,9	106,2	105,5	100,0	85,5	67,6	51,0	37,9	28,3	21,4	15,9	11,7	9,0
26	A312 - Gr. TP 317	26	137,9	137,9	137,9	133,1	123,4	117,2	115,1	112,4	111,0	109,6	108,2	106,9	106,2	105,5	100,0	85,5	67,6	51,0	37,9	28,3	21,4	15,9	11,7	9,0
27	A312 - Gr. TP 317L	27	137,9	137,9	137,9	130,3	122,0	115,8	114,5	111,7	108,9	106,9	104,8	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"	"N/A"
	1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20	21	22	23	24	25	26

								t =	593		621,0
								S =	66,9		53,1

							Table A-1. Basic alowable stresses in tension for metals (Page 157 - 161) de ASME B31.3-2002

	ASME B31.3-2002		Table A-1. Basic alowable stresses in tension for metals (Page 157 - 161)

	Allowable stress as function of temperature [MPa]
				TEMPERATURE °C
	Spec	Grade	38	93	149	204	260	316	343	371	399	427	454	482	510	538	566	593	621	649	677	704	732	760	788	816
1	A 53	Gr. A	110,3	110,3	110,3	110,3
2	A 53	A	110,3	110,3	110,3	110,3	110,3	102,0	100,0	99,3	73,8	64,1	54,5	44,8	31,0	17,2	11,0	6,9
3	A 53	B	137,9	137,9	137,9	137,9	130,3	119,3	117,2	113,8	89,6	74,5	60,0	44,8	31,0	17,2
4	A 106	A	110,3	110,3	110,3	110,3	110,3	102,0	100,0	99,3	73,8	64,1	54,5	44,8	31,0	17,2	11,0	6,9
5	A106	B	137,9	137,9	137,9	137,9	130,3	119,3	117,2	113,8	89,6	74,5	60,0	44,8	31,0	17,2
6	A106	C	160,6	160,6	160,6	157,9	148,9	135,8	133,8	132,4	102,0	82,7
7	API 5L	A	110,3	110,3	110,3	110,3
8	API 5L	A25	103,4	103,4	100,0	95,1
9	API 5L	B	137,9	137,9	137,9	137,9	130,3	119,3	117,2	113,8	89,6	74,5	60,0	44,8	31,0	17,2	11,0	6,9
10	API 5L	X42	137,9	137,9	137,9	137,9
11	API 5L	X46	144,8	144,8	144,8	144,8
12	API 5L	X52	151,7	151,7	151,7	151,7
13	API 5L	X56	163,4	163,4	163,4	163,4
14	API 5L	X60	172,4	1482,4	172,4	172,4
15	API 5L	X65	177,2	177,2	177,2	177,2
16	API 5L	X70	188,2	188,2	188,2	188,2
17	API 5L	X80	206,8	206,8	206,8	206,8
18	A312	TP 304	137,9	137,9	137,9	128,9	120,7	113,1	111,7	110,3	107,6	104,8	102,7	100,7	99,3	95,1	84,1	66,9	53,1	41,4	32,4	25,5	20,0	15,9	12,4	9,7
19	A312	TP 304L	115,1	115,1	115,1	108,9	102,0	96,5	94,5	93,1	91,7	89,6	88,3	82,0	68,3	53,8	43,4	35,2	27,6	22,1	17,9	14,5	11,7	7,6	6,9	6,2
20	A312	TP 304H	137,9	137,9	137,9	128,9	120,7	113,1	111,7	110,3	107,6	104,8	102,7	100,7	99,3	95,1	84,1	66,9	53,1	41,4	32,4	25,5	20,0	15,9	12,4	9,7
21	A312	TP 309	137,9	137,9	137,9	137,9	137,9	132,4	129,6	126,2	124,1	120,7	100,7	95,8	86,2	72,4	58,6	44,8	34,5	26,2	20,0	15,9	12,4	9,0	6,2	4,8
22	A312	TP 310	137,9	137,9	137,9	137,9	137,9	132,4	129,6	126,2	124,1	120,7	100,7	95,8	86,2	75,8	49,0	34,5	24,8	17,2	10,3	5,5	3,4	2,8	2,1	1,4
23	A312	TP 316	137,9	137,9	137,9	133,1	123,4	117,2	115,1	112,4	111,0	109,6	108,2	106,9	106,2	105,5	100,0	85,5	67,6	51,0	37,9	28,3	21,4	15,9	11,7	9,0
24	A312	TP 316L	115,1	115,1	115,1	106,9	99,3	93,1	91,0	88,9	86,9	85,5	83,4	81,4	79,3	77,2	74,5	70,3	60,7	44,1	32,4	24,1	17,2	12,4	9,0	6,9
25	A312	TP 316H	137,9	137,9	137,9	133,1	123,4	117,2	115,1	112,4	111,0	109,6	108,2	106,9	106,2	105,5	100,0	85,5	67,6	51,0	37,9	28,3	21,4	15,9	11,7	9,0
26	A312	TP 317	137,9	137,9	137,9	133,1	123,4	117,2	115,1	112,4	111,0	109,6	108,2	106,9	106,2	105,5	100,0	85,5	67,6	51,0	37,9	28,3	21,4	15,9	11,7	9,0
27	A312	TP 317L	137,9	137,9	137,9	130,3	122,0	115,8	114,5	111,7	108,9	106,9	104,8

	ASME B31.3-2006		Table A-1. Basic alowable stresses in tension for metals (Page 157 - 161)					Carbon steel pipes and tubes. Pag. 140- 144

	Allowable stress as function of temperature [ksi]
	1 ksi =	6,89476	Mpa	TEMPERATURE °C
				38	93	149	204	260	316	343	371	399	427	454	482	510	538	566	593	621	649	677	704	732	760	788	816
				Temperature °F
	Material	Spec	Grade	100	200	300	400	500	600	650	700	750	800	850	900	950	1000	1050	1100	1150	1200	1250	1300	1350	1400	1450	1500
	Type F	A 53	Gr. A, Type F	16	16	16	16
		A 53	A	16	16	16	16	16	14,8	14,5	14,4	10,7	9,3	7,9	6,5	4,5	2,5	1,6	1
		A 53	B	20	20	20	20	18,9	17,3	17	16,5	13	10,8	8,7	6,5	4,5	2,5	1,6	1
		A 106	A	16	16	16	16	16	14,8	14,5	14,4	10,7	9,3	7,9	6,5	4,5	2,5	1,6	1
		A106	B	20	20	20	20	18,9	17,3	17	16,5	13	10,8	8,7	6,5	4,5	2,5	1,6	1
		A106	C	23,3	23,3	23,3	22,9	21,6	19,7	19,4	19,2	14,8	12
		API 5L	A	16	16	16	16	16	14,8	14,5	14,4	10,7	9,3	7,9	6,5	4,5	2,5	1,6	1
	Butt weld	API 5L	A25	15	15	14,5	13,8
		API 5L	B	20	20	20	20	18,9	17,3	17	16,5	13	10,8	8,7	6,5	4,5	2,5	1,6	1
		API 5L	X42	20	20	20	20
		API 5L	X46	21	21	21	21
		API 5L	X52	22	22	22	22
		API 5L	X56	23,7	23,7	23,7	23,7
		API 5L	X60	25	215	25	25
		API 5L	X65	25,7	25,7	25,7	25,7
		API 5L	X70	27,3	27,3	27,3	27,3
		API 5L	X80	30	30	30	30
1		A312	TP 304	20	20	20	18,7	17,5	16,4	16,2	16	15,6	15,2	14,9	14,6	14,4	13,8	12,2	9,7	7,7	6	4,7	3,7	2,9	2,3	1,8	1,4
2		A312	TP 304L	16,7	16,7	16,7	15,8	14,8	14	13,7	13,5	13,3	13	12,8	11,9	9,9	7,8	6,3	5,1	4	3,2	2,6	2,1	1,7	1,1	1	0,9
3		A312	TP 304H	20	20	20	18,7	17,5	16,4	16,2	16	15,6	15,2	14,9	14,6	14,4	13,8	12,2	9,7	7,7	6	4,7	3,7	2,9	2,3	1,8	1,4
4		A312	TP 309	20	20	20	20	20	19,2	18,8	18,3	18	17,5	14,6	13,9	12,5	10,5	8,5	6,5	5	3,8	2,9	2,3	1,8	1,3	0,9	0,7
5		A312	TP 310	20	20	20	20	20	19,2	18,8	18,3	18	17,5	14,6	13,9	12,5	11	7,1	5	3,6	2,5	1,5	0,8	0,5	0,4	0,3	0,2
6		A312	TP 316	20	20	20	19,3	17,9	17	16,7	16,3	16,1	15,9	15,7	15,5	15,4	15,3	14,5	12,4	9,8	7,4	5,5	4,1	3,1	2,3	1,7	1,3
7		A312	TP 316L	16,7	16,7	16,7	15,5	14,4	13,5	13,2	12,9	12,6	12,4	12,1	11,8	11,5	11,2	10,8	10,2	8,8	6,4	4,7	3,5	2,5	1,8	1,3	1
8		A312	TP 316H	20	20	20	19,3	17,9	17	16,7	16,3	16,1	15,9	15,7	15,5	15,4	15,3	14,5	12,4	9,8	7,4	5,5	4,1	3,1	2,3	1,7	1,3
9		A312	TP 317	20	20	20	19,3	17,9	17	16,7	16,3	16,1	15,9	15,7	15,5	15,4	15,3	14,5	12,4	9,8	7,4	5,5	4,1	3,1	2,3	1,7	1,3
10		A312	TP 317L	20	20	20	18,9	17,7	16,8	16,6	16,2	15,8	15,5	15,2

								ASME B31.3-2002
								Table A-1. Basic alowable stresses in tension for metals (Page 157 - 161)

								38	93	149	204	260	316	343	371	399	427	454	482	510	538	566	593

								to
								Material	Spec	Grade	100	200	300	400	500	600	650	700	750	800	850	900	950	1000	1050	1100
								A 285 Gr. A	A 134	…	15	14,6	14,2	13,7	13	11,8	11,6	11,5	10,3	9	7,8	6,6
								A 285 Gr. A	A 672	A45	15	14,6	14,2	13,7	13	11,8	11,6	11,5	10,3	9	7,8	6,5	4,5	2,5	1,6	1

								Butt weld	API 5L	A25	15	415	154,5	13,8	-
								smls	API 5L	A25	15	415	154,5	13,8	-

								Type F	A 53	Gr. A	16	16	16	16	16	-

								A 53	A	16	16	16	16	16	14,8	14,5	14,4	10,7	9,3	7,9	6,5	4,5	2,5	1,6	1
								A 106	A	16	16	16	16	16	14,8	14,5	14,4	10,7	9,3	7,9	6,5	4,5	2,5	1,6	1
								A 135	A	16	16	16	16	16	14,8	14,5	14,4	10,7	9,3	7,9	6,5	4,5	2,5	1,6	1
								A 369	FPA	16	16	16	16	16	14,8	14,5	14,4	10,7	9,3	7,9	6,5	4,5	2,5	1,6	1
								API 5L	A	16	16	16	16	16	14,8	14,5	14,4	10,7	9,3	7,9	6,5	4,5	2,5	1,6	1

								A 285 Gr. B	A 134		16,7	16,4	16	15,4	14,6	13,3	13,1	13	11,2	9,6	8,1	6,5	-
								A 285 Gr. B	A 672	A 50	16,7	16,4	16	15,4	14,6	13,3	13,1	13	11,2	9,6	8,1	6,5	4,5	2,5	1,6	1
								285 Gr. B	A 134		18,3	18,3	17,7	17,2	16,2	14,8	14,5	14,4	12	10,2	8,3	6,5	-

								A 516 Gr. 60	A 671	CC60	20	19,5	19,8	18,3	17,3	15,8	15,5	15,4	13	10,8	8,7	6,5	4,5	2,5	-
								A 515 Gr. 60	A 671	C860	20	19,5	19,8	18,3	17,3	15,8	15,5	15,4	13	10,8	8,7	6,5	4,5	2,5	1,6	1
								A 515 Gr. 61	A 672	B60	20	19,5	19,8	18,3	17,3	15,8	15,5	15,4	13	10,8	8,7	6,5	4,5	2,5	1,6	1
								A 516 Gr. 62	A 672	C60	20	19,5	19,8	18,3	17,3	15,8	15,5	15,4	13	10,8	8,7	6,5	4,5	2,5	1,6	1

								A 53	B	20	20	20	20	18,9	17,3	17	16,5	13	10,8	8,7	6,5	4,5	2,5	-
								A106	B	20	20	20	20	18,9	17,3	17	16,5	13	10,8	8,7	6,5	4,5	2,5	-
								A 333	6	20	20	20	20	18,9	17,3	17	16,5	13	10,8	8,7	6,5	4,5	2,5	-
								A 334	6	20	20	20	20	18,9	17,3	17	16,5	13	10,8	8,7	6,5	4,5	2,5	-
								A 369	FPB	20	20	20	20	18,9	17,3	17	16,5	13	10,8	8,7	6,5	4,5	2,5	-
								A 381	Y35	20	20	20	20	18,9	17,3	17	16,5	13	10,8	8,7	6,5	4,5	2,5	-
								API 5L	B	20	20	20	20	18,9	17,3	17	16,5	13	10,8	8,7	6,5	4,5	2,5	-

								100	200	300	400	500	600	650	700	750	800	850	900	950	1000	1050	1100
								API 5L	X42	20	20	20	20
								API 5L	X46	21	21	21	21
								API 5L	X52	22	22	22	22
								API 5L	X56	23,7	23,7	23,7	23,7

								100	200	300	400	500	600	650	700	750	800	850	900	950	1000	1050	1100
								A 516 Gr. 65	A 671	CC65	21,7	21,3	20,7	20	18,9	17,3	17	16,8	13,9	11,4	9	6,5	4,5	2,5	-
								A 515 Gr. 65	A 671	C865	21,7	21,3	20,7	20	18,9	17,3	17	16,8	13,9	11,4	9	6,5	4,5	2,5	1,6	1
								A 515 Gr. 65	A 672	B65	21,7	21,3	20,7	20	18,9	17,3	17	16,8	13,9	11,4	9	6,5	4,5	2,5	1,6	1
								A 516 Gr. 65	A 672	C65	21,7	21,3	20,7	20	18,9	17,3	17	16,8	13,9	11,4	9	6,5	4,5	2,5	1,6	1

								100	200	300	400	500	600	650	700	750	800	850	900	950	1000	1050	1100
								A 516 GR. 70	A 671	CC70	23,1	22,5	21,7	20,5	48,7	18,4	18,3	14,8	12	9,3	6,5	4,5	2,5	-
								A 515 GR. 70	A 671	CB70	23,1	22,5	21,7	20,5	48,7	18,4	18,3	14,8	12	9,3	6,5	4,5	2,5	1,6	1
								A 515 GR. 70	A 672	B70	23,1	22,5	21,7	20,5	48,7	18,4	18,3	14,8	12	9,3	6,5	4,5	2,5	1,6	1
								A 516 GR. 70	A 672	C70	23,1	22,5	21,7	20,5	48,7	18,4	18,3	14,8	12	9,3	6,5	4,5	2,5	1,6	1

								A106	C	23,3	23,3	23,3	22,9	21,6	19,7	19,4	19,2	14,8	12	-

								API 5L	X60	25	25	25	25
								API 5L	X65	25,7	25,7	25,7	25,7
								API 5L	X70	27,3	27,3	27,3	27,3
								API 5L	X80	30	30	30	30

## 4. Lambda
			Table C			D7:CD8
			ASME B31.3
			Table C-1
			Thermal expansion coefficient " l " [m/(m*K)] for metals
	5		Temperatura °C
	25Cr-20Ni		2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20	21	22	23	24	25	26	27	28	29	30	31	32	33	34	35	36	37	38	39	40	41	42	43	44	45	46	47	48	49	50	51	52	53	54	55	56	57	58	59	60	61	62	63	64	65	66	67	68	69	70	71	72	73	74	75	76	77	78	79	80
	Material		-536	-522	-508	-494	-480	-466	-452	-438	-424	-411	-397	-383	-369	-355	-341	-327	-313	-299	-286	-272	-258	-247	-230	-216	-202	-188	-174	-161	-147	-133	-119	-105	-91	-77	-63	-49	-36	-22	-8	6	20	34	48	62	76	89	103	117	131	145	159	173	187	201	214	228	242	256	270	284	298	312	326	339	353	367	381	395	409	423	437	451	464	478	492	506	520	534	548
	1		2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20	21	22	23	24	25	26	27	28	29	30	31	32	33	34	35	36	37	38	39	40	41	42	43	44	45	46	47	48	49	50	51	52	53	54	55	56	57	58	59	60	61	62	63	64	65	66	67	68	69	70	71	72	73	74	75	76	77	78	79	80
1	Carbon Steel Carbon-Moly- Low-Chrome Through 3Cr-Mo)	1	-	-	-	-	-	9,0E-06	9,1E-06	9,2E-06	9,3E-06	9,4E-06	9,5E-06	9,7E-06	9,9E-06	1,0E-05	1,0E-05	1,0E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,2E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	-	-	-	-
2	5Cr-MoThrough9Cr-Mo	2	-	-	-	-	-	8,4E-06	8,5E-06	8,6E-06	8,7E-06	8,8E-06	9,0E-06	9,2E-06	9,3E-06	9,5E-06	9,5E-06	9,7E-06	9,9E-06	9,9E-06	9,9E-06	1,0E-05	9,8E-06	1,0E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	-	-	-	-
3	AusteniticStainlessSteels18Cr-8Ni	3	-	-	-	-	-	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,6E-05	1,6E-05	1,5E-05	1,5E-05	1,5E-05	1,6E-05	1,6E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05
4	12Cr,17Cr,27Cr	4	-	-	-	-	-	7,7E-06	7,8E-06	7,8E-06	7,9E-06	8,0E-06	8,1E-06	8,3E-06	8,5E-06	8,5E-06	8,6E-06	8,8E-06	9,0E-06	9,0E-06	9,0E-06	9,0E-06	9,0E-06	9,4E-06	1,0E-05	9,8E-06	9,9E-06	9,9E-06	9,9E-06	1,0E-05	1,0E-05	1,0E-05	1,0E-05	1,0E-05	1,0E-05	1,0E-05	1,0E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	-	-	-	-
5	25Cr-20Ni	5	-	-	-	-	-	-	-	-	-	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	-	-	-	-
6	UNSN04400Monel67Ni-30Cu	6						9,9E-06	1,0E-05	1,0E-05	1,1E-05	1,1E-05	1,1E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,5E-05	1,5E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	-	-	-	-
7	3.5Ni	7						8,5E-06	8,8E-06	9,0E-06	9,2E-06	9,5E-06	9,8E-06	9,9E-06	1,0E-05	1,0E-05	1,0E-05	1,0E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,2E-05	1,1E-05	1,1E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,4E-05	1,4E-05	1,4E-05	-	-	-	-	-	-	-	-	-
8	CopperandCopperAlloys	8	1,1E-05	1,2E-05	1,2E-05	1,3E-05	1,4E-05	1,4E-05	1,4E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,7E-05	-	-	-	-	-	-	-	-	-
9	Aluminum	9	-	-	-	-	-	1,8E-05	1,8E-05	1,8E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	2,0E-05	2,0E-05	2,0E-05	2,0E-05	2,1E-05	2,1E-05	2,1E-05	2,1E-05	2,1E-05	2,2E-05	2,3E-05	2,3E-05	2,3E-05	2,3E-05	2,3E-05	2,3E-05	2,4E-05	2,4E-05	2,4E-05	2,4E-05	2,4E-05	2,4E-05	2,5E-05	2,5E-05	2,5E-05	2,5E-05	2,5E-05	2,5E-05	2,5E-05	2,5E-05	2,6E-05	-	-	-	-	-	-	-	-	-
10	GrayCastIron	10	-	-	-	-	-	-	-	-	-	1,1E-05	1,0E-05	1,0E-05	1,0E-05	1,0E-05	1,0E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	-	-	-	-	-	-	-	-	-
11	Bronze	11	-	-	-	-	-	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,7E-05	2,0E-05	1,7E-05	1,6E-05	1,7E-05	1,7E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	2,0E-05	2,0E-05	2,0E-05	-	-	-	-	-	-	-	-	-
12	Brass	12	-	-	-	-	-	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,8E-05	1,7E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	1,9E-05	2,0E-05	2,0E-05	2,0E-05	2,0E-05	2,0E-05	2,0E-05	2,0E-05	2,0E-05	2,0E-05	2,1E-05	2,1E-05	2,1E-05	2,1E-05	2,1E-05	2,1E-05	2,1E-05	2,1E-05	2,1E-05	-	-	-	-	-	-	-	-	-
13	70Cu-30Ni	13	-	-	-	-	-	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,3E-05	1,3E-05	1,3E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,5E-05	1,6E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	-	-	-	-	-	-	-	-	-
14	UNSN08XXXSeriesNi-Fe-Cr	14	-	-	-	-	-	-	-	-	-	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,5E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,6E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,7E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05	1,8E-05
15	UNSN06XXXSeriesNi-Cr-Fe	15	-	-	-	-	-	-	-	-	-	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,4E-05	1,5E-05	1,5E-05	-	-	-	-	-	-	-	-	-
16	DuctileIron	16	-	-	-	-	-	-	-	-	-	8,4E-06	8,6E-06	8,8E-06	8,9E-06	9,2E-06	9,4E-06	9,6E-06	9,8E-06	9,9E-06	7,7E-06	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,1E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,2E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	1,3E-05	-	-	-	-	-	-	-	-	-

			VLOOKUP(D62;$'4. Lambda'.A9:$'4. Lambda'.CD24;D64)							Col_A =	HLOOKUP(D61; $'4. Lambda'.D7:$'4. Lambda'.CD8; 2)
											t		D7:CD8		Row 2
			VLOOKUP( D62; $'4. Lambda'.A9:$'4. Lambda'.CD24 ; D64)								38
										Col_A =	43
				Row 2		A9:CD24					for t = 34
				5Cr

## 5. Elasticity modules
	Table B. Young Modulus of Elasticity E [Pa]
	Metal	Temperature (oC)					Metal	Temperature (oC)
	1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16
	1	-200	-129	-73	21	93	149	204	260	316	371	427	482	538	593	649			-200	-129	-73	21	93	149	204	260	316	371	427	482	538	593	649
	1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	3	4					5	6	7	8	9
1	Carbon steel C <= 0.3%	2,2E+11	2,1E+11	2,1E+11	2,0E+11	2,0E+11	2,0E+11	1,9E+11	1,9E+11	1,8E+11	1,8E+11	1,7E+11	1,5E+11	1,4E+11	1,2E+11	"N/A"		Carbon steel C <= 0.3%	31,4	30,8	30,2	29,5	28,8	28,3	27,7	27,3	26,7	25,5	24,2	22,4	20,4	18
2	Carbon steel C => 0.3%	2,2E+11	2,1E+11	2,1E+11	2,0E+11	2,0E+11	1,9E+11	1,9E+11	1,9E+11	1,8E+11	1,7E+11	1,7E+11	1,5E+11	1,4E+11	1,2E+11	1,1E+11		Carbon steel C => 0.3%	31,2	30,6	30	29,3	28,6	28,1	27,5	27,1	26,5	25,3	24	22,2	20,2	17,9	15,4
3	Carbon-moly steels	2,1E+11	2,1E+11	2,1E+11	2,0E+11	2,0E+11	1,9E+11	1,9E+11	1,9E+11	1,8E+11	1,7E+11	1,6E+11	1,5E+11	1,4E+11	1,2E+11	1,1E+11		Carbon-moly steels	31,1	30,5	29,9	29,2	28,5	28	27,4	27	26,4	25,3	23,9	22,2	20,1	17,8	15,3
4	Nickel steels Ni 2% - 9%	2,0E+11	2,0E+11	2,0E+11	1,9E+11	1,9E+11	1,8E+11	1,8E+11	1,8E+11	1,7E+11	1,7E+11	1,6E+11	"N/A"	"N/A"	"N/A"	"N/A"		Nickel steels Ni 2% - 9%	29,6	29,1	28,5	27,8	27,1	26,7	26,1	25,7	25,2	24,6	23
5	Cr-Mo steels Cr 1/2% - 2%	2,2E+11	2,1E+11	2,1E+11	2,0E+11	2,0E+11	2,0E+11	1,9E+11	1,9E+11	1,9E+11	1,8E+11	1,8E+11	1,7E+11	1,6E+11	1,6E+11	1,5E+11		Cr-Mo steels Cr 1/2% - 2%	31,6	31	30,4	29,7	29	28,5	27,9	27,5	26,9	26,3	25,5	24,8	23,9	23	21,8
6	Cr-Mo steels Cr 2 1/4% - 3%	2,2E+11	2,2E+11	2,2E+11	2,1E+11	2,1E+11	2,0E+11	2,0E+11	2,0E+11	1,9E+11	1,9E+11	1,8E+11	1,8E+11	1,7E+11	1,6E+11	1,6E+11		Cr-Mo steels Cr 2 1/4% - 3%	32,6	32	31,4	30,6	29,8	29,4	28,8	28,3	27,7	27,1	26,3	25,6	24,6	23,7	22,5
7	Cr-Mo steels Cr 5% - 9%	2,3E+11	2,2E+11	2,2E+11	2,1E+11	2,1E+11	2,0E+11	2,0E+11	2,0E+11	1,9E+11	1,9E+11	1,8E+11	1,7E+11	1,6E+11	1,4E+11	1,3E+11		Cr-Mo steels Cr 5% - 9%	32,9	32,3	31,7	30,9	30,1	29,7	29	28,6	28	27,3	26,1	24,7	22,7	20,4	18,2
8	Chromium steels Cr 12%, 17%, 27%	2,2E+11	2,1E+11	2,1E+11	2,0E+11	2,0E+11	1,9E+11	1,9E+11	1,8E+11	1,8E+11	1,8E+11	1,7E+11	1,6E+11	1,5E+11	1,3E+11	1,1E+11		Chromium steels Cr 12%, 17%, 27%	31,2	30,7	30,1	29,2	28,5	27,9	27,3	26,7	26,1	25,6	24,7	23,2	21,5	19,1	16,6
9	Austenitic steels (TP304, 310, 316, 321, 347)	2,1E+11	2,0E+11	2,0E+11	2,0E+11	1,9E+11	1,9E+11	1,8E+11	1,8E+11	1,7E+11	1,7E+11	1,7E+11	1,6E+11	1,6E+11	1,5E+11	1,5E+11		Austenitic steels (TP304, 310, 316, 321, 347)	30,3	29,7	29,1	28,3	27,6	27	26,5	25,8	25,3	24,8	24,1	23,5	22,8	22,1	21,2

	Cast iron					Cast iron
	Gray cast iron				1,3E+01	1,3E+01	1,3E+01	1,3E+01	1,2E+01	1,2E+01	1,1E+01	1,0E+01					Gray cast iron				13,4	13,2	12,9	12,6	12,2	11,7	11	10,2

	http://www.engineeringtoolbox.com/young-modulus-d_773.html
		Mpsi =	6,9E+09	Pa

## 6.CS_Imp
1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17
2
3	Pipe Thickness [mm], according ASME B36.10M
4
5							ASME B36.10M SCHEDULE / IDENTIFICATION											Application			Dn =	10	in
6	Size	dext	5	10	20	30	40	60	80	100	120	140	160	STD	XS	XXS		(with input validation)			SCH =	XXS	-
7	1/2	21,3	1,65	2,11	-	2,41	2,77	-	3,73	-	0	-	4,78	2,77	3,73	7,47		di =	Pipe_Imp_CS_Dint_dn_sch			#NAME?	mm
8	3/4	26,7	1,65	2,11	-	2,41	2,87	-	3,91	-	0	-	5,56	2,87	3,91	7,82		de =	Pipe_Imp_CS_Dext_dn			#NAME?	mm
9	1	33,4	1,65	2,77	-	2,9	3,38	-	4,55	-	0	-	6,35	3,38	4,55	9,09		s =	Pipe_Imp_CS_Thickness_dn_sch			#NAME?	mm
10	1 1/4	42,2	1,65	2,77		2,97	3,56		4,85				6,35	3,56	4,85	9,7
11	1 1/2	48,3	1,65	2,77	-	3,18	3,68	-	5,08	-	0	-	7,14	3,68	5,08	10,15
12	2	60,3	1,65	2,77	-	3,18	3,91	-	5,54	-	0	-	8,74	3,91	5,54	11,07		Application			Dn =	16	in
13	2 1/2	73	2,11	3,05		4,78	5,16		7,01				9,53	5,16	7,01	14,02
14	3	88,9	2,11	3,05	-	4,78	5,49	-	7,62	-	0	-	11,13	5,49	7,62	15,24		(without input validation)			SCH =	81
15	3 1/2	101,6	2,11	3,05		4,78	5,74		8,08					5,74	8,08
16	4	114,3	2,11	3,05	-	4,78	6,02	-	8,56	-	11,13	-	13,49	6,02	8,56	17,12		di =	Pipe_Imp_CS_Dint_dn_sch			N/A	mm
17	5	141,3	2,77	3,4	-	-	6,55	-	9,53	-	12,7	-	15,88	6,55	9,53	19,05		de =	Pipe_Imp_CS_Dext_dn			559	mm
18	6	168,3	2,77	3,4	-	-	7,11	-	10,97	-	14,27	-	18,26	7,11	10,97	21,95		s =	Pipe_Imp_CS_Thickness_dn_sch			N/A	mm
19	8	219,1	2,77	3,76	6,35	7,04	8,18	10,31	12,7	15,09	18,26	20,62	23,01	8,18	12,7	22,23		The shedule entered is wrong
20	10	273	3,4	4,19	6,35	7,8	9,27	12,7	15,09	18,26	21,44	25,4	28,58	9,27	12,7	25,4
21	12	323,8	3,96	4,57	6,35	8,38	10,31	14,27	17,48	21,44	25,4	28,58	33,32	9,53	12,7	25,4
22	14	355,6	3,96	6,35	7,92	9,53	11,13	15,09	19,05	23,83	27,79	31,75	35,71	9,53	12,7	-
23	16	406,4	4,19	6,35	7,92	9,53	12,7	16,66	21,44	26,19	30,96	36,53	40,49	9,53	12,7	-
24	18	457	4,19	6,35	7,92	11,13	14,27	19,05	23,83	29,36	34,93	39,67	45,24	9,53	12,7	-
25	20	508	4,78	6,35	9,53	12,7	15,09	20,62	26,19	32,54	38,1	44,45	50,01	9,53	12,7	-
26	22	559	4,78	6,35	9,53	12,7	-	22,23	28,58	34,93	41,28	47,63	53,98	9,53	12,7	-
27	24	610	5,54	6,35	9,53	14,27	17,48	24,61	30,96	38,89	46,02	52,37	59,54	9,53	12,7	-
28	26	660	-	7,92	12,7	15,88	-	-	-	-	-	-	-	9,53	12,7	-
29	28	711	-	7,92	12,7	-	-	-	-	-	-	-	-	9,53	12,7	-
30	30	762	6,35	7,92	12,7	15,88	-	-	-	-	-	-	-	9,53	12,7	-
31	32	813	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-	9,53	12,7	-
32	34	864	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-	9,53	12,7	-
33	36	914	-	7,92	12,7	15,88	19,05	-	-	-	-	-	-	9,53	12,7	-
34	38	965	-	-	-	-	-	-	-	-	-	9,53	12,7	-
35	40	1016	-	-	-	-	-	-	-	-	-	9,53	12,7	-
36	42	1067	-	-	-	-	-	-	-	-	-	9,53	12,7	-
	44	1118	-	-	-	-	-	-	-	-	-	9,53	12,7	-
	46	1168	-	-	-	-	-	-	-	-	-	9,53	12,7	-
39	48	1219	-	-	-	-	-	-	-	-	-	9,53	12,7	-

	Carbon steel pipes
	dn	Sc -
	in
	1/2	5
	3/4	10
	1	20
	1 1/2	30
	2	40
	3	60
	4	80
	5	100
	6	120
	8	140
	10	160
	12	STD
	14	XS
	16	XXS			Carbon steel pipes.
	18				dn: 1/2,3/4,1,1 1/2,2,3,4,5,6,8,10,12,14,16,18,20,22,24,26,28,30,32,34,36,38,40,42,44,46,48. Sch:5,10,20,30,40,60,80,100,120,140,160,STD,XS,XXS
	20
	22
	24
	26
	28
	30
	32
	34
	36
	38
	40
	42
	44
	46
	48

## 6. Spiraxsarco
http://pointing.spiraxsarco.com/resources/steam-engineering-tutorials/steam-distribution/pipe-expansion-and-support.asp

					For expansion "DL" (mm), and a
					pipe nominal diameter "dn" (in),
					Spiraxsarco graph provides an
					expansionloop width "W" (m).

					DL =	90	mm
					dn =	273	mm
					Estimated value from Fig. 10.4
					W =	2,55	m

					spiraxsarco. Expansion loop capacity

http://pointing.spiraxsarco.com/resources/steam-engineering-tutorials/steam-distribution/pipe-expansion-and-support.asp

Example 10.4.2

Using Figure 10.4.1. Find the approximate expansion from 15°C, of 100 metres of carbon steel pipework used to distribute steam at 265°C.

Temperature difference is 265 - 15°C = 250°C.

Where the diagonal temperature difference line of 250°C cuts the horizontal pipe length line at 100 m, drop a vertical line down. For this example an approximate expansion of 330 mm is indicated.

Fig. 10.4.1 A chart showing the expansion in various steel pipe lengths at various temperature differences
Table 10.4.2 Temperature of saturated steam

## 7. Victaulic
http://static.victaulic.com/assets/uploads/literature/26.02-SPA.pdf
	Vitaulic equation for an expansion loop
					H =
					1988 ASHRAE Handbook, EQUIPMENT					E: Elasticity module of material
					d: exterior pipe diameter
					ftot: total pipe expansion
					S: Allowable stress of material

					5W =	L
					W =	L/5

					H =	2*W
					H =	2 * L / 5
					H =	0.4 * L

					Equation deducted in sheet 2

## 8. Properties.
http://www.engineeringtoolbox.com/pipes-temperature-expansion-coefficients-d_48.html

Temperature Expansion Coefficients for some common Piping Materials

Expansion coefficients for some common materials used for pipes and tubes - like aluminum, carbon steel, cast iron, PVC, HDPE and more

Expansion coefficients that can be used to calculate temperature expansion of pipes and tubes - are indicated in the table below:

Material	Expansion Coefficients					THERMAL		http://www.harvel.com/piping-systems/gf-harvel-pvc-industrial-pipe
	10-6 in/in oF	10-6 m/m oC					Coefficient of Linear Expansion
Aluminum	12,8	23,1					Coefficient of Linear Expansion	in/in/°F	2.9 x 10-5	2.8 x 10-5	ASTM D696
Carbon Steel	6,5	11,7					l =	2,8E-05	in / (in / ºF)
Cast Iron	5,9	10,6					l =	5,04E-05	m/(m*ªC)
Copper	9,3	16,8
Stainless Steel	9,9	17,8
ABS Acrylonitrile butadiene styrene	35	63
HDPE High density polyethylene	67	120
PE Polyethylene	83	150
CPVC Chlorinated polyvinyl chloride	44	79
PVC Polyvinyl chloride	28	50,4

http://www.engineeringtoolbox.com/young-modulus-d_417.html

Material	Tensile Modulus		Ultimate Tensile Strength	Yield Strength
	(Young's Modulus, Modulus of Elasticity)		- Su -	- Sy -
	- E -		(106 N/m2, MPa)	(106 N/m2, MPa)					http://www.harvel.com/piping-systems/gf-harvel-pvc-industrial-pipe
	(106 psi)	(109 N/m2, GPa)					Tensile Modulus of Elasticity @ 73°F, for PVC
Polyvinylchloride (PVC)		2.4 - 4.1				E =				Tensile Modulus of Elasticity @ 73°F	PSI	420.000	430.000	ASTM D638
ABS plastics		1.4 - 3.1	40					E =	4,3.E+05	psi
Acetals		2,8	65					E =	3,0.E+03	Mpa
Acrylic		3,2	70					E =	3E+09	Pa
Aluminum Bronze		120
Aluminum	10	69	110	95
Aluminum Alloys	10,2
Antimony	11,3
Aramid		70 - 112
Beryllium (Be)	42	287
Beryllium Copper	18
Bismuth	4,6
Bone, compact		18	170
			(compression)
Bone, spongy		76
Boron				3100
Brass		102 - 125	250
Brass, Naval		100
Bronze		96 - 120
CAB		0,8
Cadmium	4,6
Carbon Fiber Reinforced Plastic		150
Carbon nanotube, single-walled		1000+
Cast Iron 4.5% C, ASTM A-48			170
Cellulose, cotton, wood pulp and regenerated			80 - 240
Cellulose acetate, molded			dic-58
Cellulose acetate, sheet			30 - 52
Cellulose nitrate, celluloid			50
Chlorinated polyether		1,1	39
Chlorinated PVC (CPVC)		2,9
Chromium	36
Cobalt	30
Concrete		17
Concrete, High Strength (compression)		30	40
			(compression)
Copper	17	117	220	70
Diamond (C)		1220
Douglas fir Wood		13	50
			(compression)
Epoxy resins		03-feb	26 - 85
Fiberboard, Medium Density		4
Flax fiber		58
Glass		50 - 90	50
			(compression)
Glass reinforced polyester matrix		17
Gold	10,8	74
Granite		52
Graphene		1000
Grey Cast Iron		130
Hemp fiber		35
Inconel	31
Iridium	75
Iron	28,5	210
Lead	2
Magnesium metal (Mg)	6,4	45
Manganese	23
Marble			15
MDF - Medium-density fiberboard		4
Mercury
Molybdenum (Mo)	40	329
Monel Metal	26
Nickel	31	170
Nickel Silver	18,5
Nickel Steel	29
Niobium (Columbium)	15
Nylon-6		02-abr	45 - 90	45
Nylon-66			60 - 80
Oak Wood (along grain)		11
Osmium (Os)	80	550
Phenolic cast resins			33 - 59
Phenol-formaldehyde molding compounds			45 - 52
Phosphor Bronze		116
Pine Wood (along grain)		9	40
Platinum	21,3
Plutonium	14	97
Polyacrylonitrile, fibers			200
Polybenzoxazole		3,5
Polycarbonates		2,6	52 - 62
Polyethylene HDPE (high density)		0,8	15
Polyethylene Terephthalate, PET		2 - 2.7	55
Polyamide		2,5	85
Polyisoprene, hard rubber			39
Polymethylmethacrylate (PMMA)		2.4 - 3.4
Polyimide aromatics		3,1	68
Polypropylene, PP		1.5 - 2	28 - 36
Polystyrene, PS		3 - 3.5	30 - 100
Polytehylene, LDPE (low density)		0.11 - 0.45
Polytetrafluoroethylene (PTFE)		0,4
Polyurethane cast liquid			oct-20
Polyurethane elastomer			29 - 55
Polyvinylchloride (PVC)		2.4 - 4.1
Potassium
Rhodium	42
Rubber, small strain		0.01 - 0.1
Sapphire		435
Selenium	8,4
Silicon	16	130 - 185
Silicon Carbide		450		3440
Silver	10,5
Sodium
Steel, High Strength Alloy ASTM A-514			760	690
Steel, stainless AISI 302		180	860	502
Steel, Structural ASTM-A36		200	400	250
Tantalum	27
Polytetrafluoroethylene (PTFE)		0,5
Thorium	8,5
Tin		47
Titanium	16
Titanium Alloy		105 - 120	900	730
Tooth enamel		83
Tungsten (W)		400 - 410
Tungsten Carbide (WC)		450 - 650
Uranium	24	170
Vanadium	19
Wrought Iron		190 - 210
Zinc	12

#VALUE!

Thermoplastics - Physical Properties

Physical properties of some thermoplastics like ABS, PVC, CPVC, PE, PEX, PB and PVDF

Typical properties of some common thermoplastics:

Thermoplastic	Specific Gravity	Tensile Yield Strength	Tensile Modulus	Coefficients of	Thermal Conductivity	Specific Heat	Maximum Temperature Limit
		(103 psi)	(103 psi)	Linear Expansion	(Btu in /h ft2 oF)	(Btu/lb oF)	(oF/oC)
				(106 in/in oF)
ABS	1,08	7	340	60	1,35	0,34	180/80
PVC	1,4	8	410	30	1,1	0,25	150/65		s =	8	kpsi
CPVC	1,54	8	420	35	1	0,2	210/100		s =	8000	psi
PE	0,95	3,2	120	90	3,2	0,55	160/70		s =	5,52E+07	Pa
PEX	0,94	2,8	.	90	3,2	0,55	210/100
PB	0,92	4,2	55	72	1,5	0,45	210/100
PVDF	1,76	7	220	70	1,5	0,29	300/150

1 psi (lb/in2) = 6,894.8 Pa (N/m2) - Note! You can use the pressure unit converter on this page to switch to Pa (N/m2) units.
1 (Btu/lb oF) = 4,186.8 (J/kg K) = 1 (kcal/kg oC)

## 9. U.S. Corps
U.S. Army Corps of Engineers

[8]

					1988 ASHRAE Handbook, EQUIPMENT

					H =	0.4 * ( 3 * E * dext * DL / salow)^0.5

					Pipe material design stress
					sdes =	103	MPa
					Material elasticity modulus
					E =	1,92E+05	MPa

					L0 =	145	m
					dext =	200	mm		Thermal expansion coefficient
					top =	90	ºC		a =	1,17E-05	m / (m * K)
					t0 =	4,4	ºC		Pipe material design stress
					sallow =	103	MPa
					Material elasticity modulus
					E =	1,92E+05	MPa

					Temperature difference
					Dt =	top -t0
					top =	90	ºC
					t0 =	4,4	ºC
					Dt =	85,6	K

					Linear expansion
					DL =	L0 * a * Dt
					L0 =	145	m
					a =	1,17E-05	m / (m * K)
					Dt =	85,6	K
					DL =	0,1452	m

					H =	0.4 * ( 3 * E * dext * DL / salow)^0.5					The derived equation for the loop height is
					E =	1,92E+05	MPa				Height "H" of expansion loop
					dext =	0,2	MPa				H = 0.378*( (3 * E * de * DL) / (sallow) )^0.5
					DL =	0,1452	m
					sallow =	103	MPa
					H =	5,098	m

## Ref. 7
Cantilever beam, concentrated load at free end

y =	P * L³ / (3*E*I)

## Combo-box
				rev.cjc.01.08.2018

	Select data with Combo Box form control
				Required is to obtain the value of the
1					Z-Factor for a given seismic zone, selected
				using the Drop-down list.

				3
				Seismic zone factor Z
2					Seismic zone	Factor Z
				1	0,075
				2A	0,15
				2B	0,2
	Insert					3	0,3
	It appears the Forms control box					4	0,4

				Select a seismic zone

				Corresponding Z-Factor
3			Select: Combo Box (Form Control)					Z =	0,2

				Note. If it is not required the use of a
				Drop-down list, the use of the V-lookup
				function is a much more shorter way.

				Z =	VLOOKUP(K14,K12:L16,2)
				Z =	0,2
4	Draw a box

5	Right clik box

6				Click formar control

	The Format Control window appears

	Application example

		2
		Seismic zone factor Z
		Seismic zone	Factor Z
		1	0,075
		2A	0,15
		2B	0,2
		3	0,3
		4	0,4

				(repetead)
				4	Draw a box
				5	Rigth click the box
				6	Format control
				7	Input the range and
				8	define a cell to place the link
				9	OK

7
8

9

10					10	Click the selection box
				to select a zone

	Obtain a workable number (Z-value) corresponding to the selected zone
	Insert function Index

11

12	OK

	Select the first argument row

13

14	OK

	The function arguments window appears

	In the Functions arguments window, input required data

15
16
17

18

		Z =	INDEX(E66:F70,E63,2)
		Z =	0,15

## Ref
[1]	Elementos de resistencia de materiales
	S. Timoshenko, D. H. Young
	Ed. Limusa, 1996

[2]

[3]

[4]	http://static.victaulic.com/assets/uploads/literature/26.02-SPA.pdf

[5]	http://www.spiraxsarco.com/resources/steam-engineering-tutorials/steam-distribution/pipe-expansion-and-support.asp

[5]	F(Simple drive):\Libreria\Piping\Piping Handbook (7th Edition)

[6]	http://www.engineeringtoolbox.com/young-modulus-d_773.html

	www.piping-tools.net
	Expansion_loop.xlsm

[7]	http://www.awc.org/pdf/codes-standards/publications/design-aids/AWC-DA6-BeamFormulas-0710.pdf

[8]

						U.S. Army Corps of Engineers

	http://www.publications.usace.army.mil/Portals/76/Publications/EngineerManuals/EM_1110-1-4008.pdf

## PVC_40
1	2	3	4	5	6
2		PVC pipe material		CPVC 4120
3		Dimensions according		ASTM D2846 / D2846M "Standard Specification for Chlorinated Poly(Vinyl Chloride) (CPVC)
4		Pressure according		ASTM pressure equation
5
6		Schedule 40 PVC Pipe		CPVC 4120
7		Size	de	s	P
8		in	mm	mm	bar
9		1/2	21,34	2,7686	41,1
10		3/4	26,67	2,8702	33,3
11		1	33,40	3,3782	31,0
12		1 1/4	42,16	3,556	25,4
13		1 1/2	48,26	3,683	22,8
14		2	60,33	3,9116	19,1
15		2 1/2	73,03	5,1562	21,0
16		3	88,90	5,4864	18,1
17		4	114,30	6,0198	15,3
18		5	141,30	6,5532	13,4
19		6	168,28	7,112	12,2
20		8	219,08	8,4328	11,0
21		10	273,05	9,271	9,7
22		12	323,85	10,3124	9,1

## PVC_80
1	2	3	4	5	6
2		PVC pipe material		CPVC 4120
3		Dimensions according		ASTM D2846 / D2846M "Standard Specification for Chlorinated Poly(Vinyl Chloride) (CPVC)
4		Pressure according		ASTM pressure equation
5
6		Schedule 80 PVC Pipe		CPVC 4120
7		Size	de	s	P
8		in	mm	mm	bar
9		1/2	21,34	3,7338	58,5
10		3/4	26,67	3,9116	47,4
11		1	33,40	4,5466	43,5
12		1 1/4	42,16	4,8514	35,9
13		1 1/2	48,26	5,08	32,4
14		2	60,33	5,5372	27,9
15		2 1/2	73,03	7,0104	29,3
16		3	88,90	7,62	25,9
17		4	114,30	8,5598	22,3
18		5	141,30	9,525	19,9
19		6	168,28	10,9728	19,2
20		8	219,08	12,7	17,0
21		10	273,05	15,0622	16,1
22		12	323,85	17,4498	15,7