## Resume
				Rev. cjc. 23.06.2017

	Resume of pipe functions

1	Carbon steel (dn, Imperial units)			Dn =	4	in		5	HDPE PE100 (dn, Imperial units)			Dn =	6	in
				SCH =	40	-					PN =	20	bar
	di =	Pipe_Imp_CS_Dint_dn_sch		di =	N/A	mm			di =	Pipe_Imp_HD100_Dint_Dn_PN		di =	124,2	mm
	de =	Pipe_Imp_CS_Dext_dn		de =	114,3	mm			de =	Pipe_Imp_HD100_Dext_Dn		de =	160	mm
	s =	Pipe_Imp_CS_Thickness_dn_sch		s =	N/A	mm			s =	Pipe_Imp_HD100_Thickness_Dn_PN		s =	17,9	mm

2	Carbon steel (dn, SI units)			Dn =	100	mm		6	HDPE PE100 (dn, SI units)			Dn =	110	mm
				SCH =	80	-					PN =	20	bar
	di =	Pipe_SI_CS_Dint_dn_sch		di =	N/A	mm			di =	Pipe_SI_HD100_Dint_Dn_PN		di =	85,4	mm
	de =	Pipe_SI_CS_Dext_dn		de =	114,3	mm			de =	Pipe_SI_HD100_Dext_Dn(Dn)		de =	110	mm
	s =	Pipe_SI_CS_Thickness_dn_sch		s =	N/A	mm			s =	Pipe_SI_HD100_Thickness_Dn_PN		s =	12,3	mm

3	Stainless steel (dn, SI units)			Dn =	400	mm		7	HDPE PE80 (dn, SI units)			Dn =	40	mm
				SCH =	10S	-					PN =	10	bar
	di =	Pipe_SI_SS_Dint_dn_sch		di =	396,84	mm			di =	Pipe_SI_HD80_Dint_Dn_PN		di =	32,6	mm
	de =	Pipe_SI_SS_Dext_dn		de =	406,4	mm			de =	Pipe_SI_HD80_Dext_Dn		de =	40	mm
	s =	Pipe_SI_SS_Thickness_dn_sch		s =	4,78	mm			s =	Pipe_SI_HD80_Thickness_Dn_PN		s =	3,7	mm

4	Stainless steel (dn Imperial units)			Dn =	16	in		8	HDPE PE80 (dn, Imperial units)			Dn =	1 1/4	in
				SCH =	10S	-					PN =	10	bar
	di =	Pipe_Imp_SS_Dint_Dn_SCH		di =	396,84	mm			di =	Pipe_Imp_HD80_Dint_Dn_PN		di =	32,6	mm
	de =	Pipe_Imp_SS_Dext_Dn		de =	406,4	mm			de =	Pipe_Imp_HD80_Dext_Dn		de =	40	mm
	s =	Pipe_Imp_SS_Thickness_Dn_SCH		s =	4,78	mm			s =	Pipe_Imp_HD80_Thickness_Dn_PN		s =	3,7	mm

	Darcy-Weisbach friction factor
	f =	Pipe_Friction_Factor_Rrel_Re(Rrel, Re)
	Rrel =	0,0001
	Re =	125000
	f =	0,018

## CS SS HDPE
	Note. This data is not required by the functions. The data is included in the Macros, in the Modules of the Standard Library.
						Rev. cjc. 23.06..2017
	Carbon steel pipes with nominal diameter input dn in milimeters and in inches, exterior diameter and thickness in milimeters, according ASME B36.10M

			Carbon steel pipe thickness s (mm)					Carbon steell pipes			Carbon steell pipes
dn	dn	dext	ASME B36.10M SCHEDULE					Imperial			SI
mm	"	mm	5	10	20	30	40	60	80	100	120	140	160	STD	XS	XXS		Pipe_Imp_CS_Dext_dn			Pipe_SI_CS_Dext_dn
6	1/8	10,3	0	1,24	0	1,45	1,73	0	2,41	0	0	0	0	0	0	0		Pipe_Imp_CS_Thickness_dn_sch			Pipe_SI_CS_Thickness_dn_sch
8	1/4	13,7	0	1,65	0	1,85	2,24	0	3,02	0	0	0	0	0	0	0		Pipe_Imp_CS_Dint_dn_sch			Pipe_SI_CS_Dint_dn_sch
10	3/8	17,1	0	1,65	0	1,85	2,31	0	3,2	0	0	0	0	0	0	0
15	1/2	21,3	1,65	2,11	0	2,41	2,77	0	3,73	0	0	0	4,78	2,77	3,73	7,47
20	3/4	26,7	1,65	2,11	0	2,41	2,87	0	3,91	0	0	0	5,56	2,87	3,91	7,82		dn =	2	in	dn =	100	mm
25	1	33,4	1,65	2,77	0	2,9	3,38	0	4,55	0	0	0	6,35	3,38	4,55	9,09		Sch =	XS		Sch =	XS
32	1 1/4	42,2	1,65	2,77	0	2,97	3,56	0	4,85	0	0	0	6,35	3,56	4,85	9,7
40	1 1/2	48,3	1,65	2,77	0	3,18	3,68	0	5,08	0	0	0	7,14	3,68	5,08	10,15		Dext =	60,3	MM	DEXT =	114,3	mm
50	2	60,3	1,65	2,77	0	3,18	3,91	0	5,54	0	0	0	8,74	3,91	5,54	11,07		s =	5,54	MM	S =	8,56	mm
65	2 1/2	73,0	2,11	3,05	0	4,78	5,16	0	7,01	0	0	0	9,53	5,16	7,01	14,02		Dint =	49,22	MM	DINT =	97,18	mm
80	3	88,9	2,11	3,05	0	4,78	5,49	0	7,62	0	0	0	11,13	5,49	7,62	15,24
90	3 1/2	101,6	2,11	3,05	0	4,78	5,74	0	8,08	0	0	0	-	5,74	8,08	-
100	4	114,3	2,11	3,05	0	4,78	6,02	0	8,56	0	0	0	13,49	6,02	8,56	17,12
125	5	141,3	2,77	3,4	0	0	6,55	0	9,53	0	0	0	15,88	6,55	9,53	19,05
150	6	168,3	2,77	3,4	0	0	7,11	0	10,97	0	0	0	18,26	7,11	10,97	21,95
200	8	219,1	2,77	3,76	6,35	7,04	8,18	10,31	12,7	15,09	18,26	20,62	23,01	8,18	12,7	22,23
250	10	273	3,40	4,19	6,35	7,8	9,27	12,7	15,09	18,26	21,44	25,4	28,58	9,27	12,7	25,4
300	12	323,8	3,96	4,57	6,35	8,38	10,31	14,27	17,48	21,44	25,4	28,58	33,32	9,53	12,7	25,4			Carbon steel pipe data
350	14	355,6	3,96	6,35	7,92	9,53	11,13	15,09	19,05	23,83	27,79	31,75	35,71	9,53	12,7	0			Extracted from
400	16	406,4	4,19	6,35	7,92	9,53	12,7	16,66	21,44	26,19	30,96	36,53	40,49	9,53	12,7	0			ASME B36.10M-2000
450	18	457	4,19	6,35	7,92	11,13	14,27	19,05	23,83	29,36	34,93	39,67	45,24	9,53	12,7	0			(Revision of ASME B36.10M-1996)
500	20	508	4,78	6,35	9,53	12,7	15,09	20,62	26,19	32,54	38,1	44,45	50,01	9,53	12,7	0			Table 1 Dimensions and weights of
550	22	559	4,78	6,35	9,53	12,7	0	22,23	28,58	34,93	41,28	47,63	53,98	9,53	12,7	0			welded and seamless wrought steel pipe
600	24	610	5,54	6,35	9,53	14,27	17,48	24,61	30,96	38,89	46,02	52,37	59,54	9,53	12,7	0
650	26	660	0	7,92	12,7	15,88	0	0	0	0	0	0	0	9,53	12,7	0
700	28	711	0	7,92	12,7	0	0	0	0	0	0	0	0	9,53	12,7	0
750	30	762	6,35	7,92	12,7	15,88	0	0	0	0	0	0	0	9,53	12,7	0
800	32	813	0	7,92	12,7	15,88	17,48	0	0	0	0	0	0	9,53	12,7	0
850	34	864	0	7,92	12,7	15,88	17,48	0	0	0	0	0	0	9,53	12,7	0
900	36	914	0	7,92	12,7	15,88	19,05	0	0	0	0	0	0	9,53	12,7	0
950	38	965	0	0	0	0	0	0	0	0	9,53	12,7	0
1000	40	1016	0	0	0	0	0	0	0	0	9,53	12,7	0
1050	42	1067	0	0	0	0	0	0	0	0	9,53	12,7	0
1100	44	1118	0	0	0	0	0	0	0	0	9,53	12,7	0
1150	46	1168	0	0	0	0	0	0	0	0	9,53	12,7	0
1200	48	1219,2	0	0	0	0	0	0	0	0	9,53	12,7	0

	Stainless steel thickness according ASME B36.19-1985
	Nominal diameter in milimeters and in inches
						Reference
			Stainless steel pipe thickness s (mm)					Stainless steel pipe
dn	dn	dext	Schedule					ANSI/ASME B36.19M-1985
mm	in	mm	5S	10S	40S	80S				Imperial					SI				Reaffirmed 1994
6	0,125	10,3	0	1,24	1,73	2,41					Tables 2A. Dimensions of welded and seamless steel pipe - SI units
8	0,25	13,7	0	1,65	2,24	3,02				dn =	2	in			dn =	50	mm
10	0,375	17,1	0	1,65	2,31	3,20				Sch =	10S				Sch =	10S
15	0,5	21,3	1,64	2,11	2,77	3,73
20	0,75	26,7	1,65	2,11	2,87	3,91				Dext =	60,3	mm			Dext =	60,3	mm
25	1	33,4	1,65	2,77	3,38	4,55				s =	2,77	mm			s =	2,77	mm
32	1,25	42,2	1,65	2,77	3,56	4,85				Dint =	54,76	mm			Dint =	54,76	mm
40	1,5	48,3	1,65	2,77	3,68	5,08
50	2	60,3	1,65	2,77	3,91	5,54
65	2,5	73	2,11	3,05	5,16	7,01
80	3	88,9	2,11	3,05	5,49	7,62
90	3,5	101,6	2,11	3,05	5,74	8,08
100	4	114,3	2,11	3,05	6,02	8,56
125	5	141,3	2,77	3,40	6,55	9,53
150	6	168,3	2,77	3,40	7,11	10,97
200	8	219,1	2,77	3,76	8,18	12,70
250	10	273,1	3,40	4,19	9,27	12,70
300	12	323,9	3,96	4,57	9,53	12,70
350	14	355,6	3,96	4,78	0	0
400	16	406,4	4,19	4,78	0	0
450	18	457	4,19	4,78	0	0
500	20	508	4,78	5,54	0	0
550	22	559	4,78	5,54	0	0
600	24	610	5,54	6,35	0	0
750	30	762	6,35	7,92	0	0

HDPE PE100 Thickness (mm) and (in) ISO 4427						SI

dn = Dext	dn (*)	Nominal pressures PN [bar]					dn =	90	mm
mm	in	4	6	8	10	12,5	16	20				PN =	20	bar
16	3/8	0	0	0	0	0	0	2,3	16	0
20	1/2	0	0	0	0	0	0	2,3	20	1		Dext =	90	mm
25	3/4	0	0	0	0	0	2,3	2,8	25	2		s =	10,10	mm
32	1	0	0	0	0	2,4	3	3,6	32	3		Din =	69,8	mm
40	1 1/4	0	0	0	2,4	3	3,7	4,5	40	4
50	1 1/2	0	0	2,4	3	3,7	4,6	5,6	50	5
63	2	0	2,3	3	3,8	4,7	5,8	7,1	63	6
75	2 1/2	0	2,8	3,6	4,5	5,6	6,8	8,4	75	7		Imperial
90	3	2,3	3,3	4,3	5,4	6,7	8,2	10,1	90	8
110	4	2,7	4	5,3	6,6	8,1	10	12,3	110	9		dn =	4	in
125	5	3,1	4,6	6	7,4	9,2	11,4	14	125	10		PN =	20	bar
140	5 1/2	3,5	5,1	6,7	8,3	10,3	12,7	15,7	140	11
160	6	4	5,8	7,7	9,5	11,8	14,6	17,9	160	12		Dext =	110	mm
180	7	4,4	6,6	8,6	10,7	13,3	16,4	20,1	180	13		s =	12,30	mm
200	8	4,9	7,3	9,6	11,9	14,7	18,2	22,4	200	14		Din =	85,4	mm
225	9	5,5	8,2	10,8	13,4	16,6	20,5	25,2	225	15
250	10	6,2	9,1	11,9	14,8	18,4	22,7	27,9	250	16
280	11	6,9	10,2	13,4	16,6	20,6	25,4	31,3	280	17
315	12	7,7	11,4	15	18,7	23,2	28,6	35,2	315	18
355	14	8,7	12,9	16,9	21,1	26,1	32,2	39,7	355	19
400	16	9,8	14,5	19,1	23,7	29,4	36,3	44,7	400	20
450	18	11	16,3	21,5	26,7	33,1	40,9	50,3	450	21		Note (*)
500	20	12,3	18,1	23,9	29,7	36,8	45,4	55,8	500	22		Nominal diameters in inches in
560	22	13,7	20,3	26,7	33,2	41,2	50,8	0	560	23		red colour are not defined in the
630	24	15,4	22,8	30	37,4	46,2	57,2	0	630	24		imperial denomination
710	28	17,4	25,7	33,9	42,1	52,2	0	0	710	25
800	32	19,6	29	38,1	47,4	58,8	0	0	800	26
900	36	22	32,6	42,6	53,3	0	0	0	900	27
1000	40	24,5	36,2	47,7	59,3	0	0	0	1000	28
1200	48	29,4	43,4	57,2		0	0	0	1200	29
1400	54	34,3	50,6	0		0	0	0	1400	30
1600	64	39,2	57,9	0		0	0	0	1600	31
		4	6	8	10	12,5	16	20

	http://www.soheval.cl/files/Tablas_tecnicas.pdf

	ISO 4427 PE 100 Design stress 8.0 MPa

	For info., http://www.krah.cl/wp-content/uploads/2013/10/catalogo_krah_final_baja.pdf

Thickness of HDPE PE80 pipe DIN 8074 / ISO 4427

dn = Dext	dn (*)	Nominal pressure PN [bar]
mm	in	2 1/2	3,2	4	6	10	16		SI			Imperial
16	3/8	0	0	0	0	0	2,2
20	1/2	0	0	0	0	1,9	2,8		dn =	40	mm	dn =	1 1/4	in
25	3/4	0	0	0	0	2,3	3,5		PN =	10	bar	PN =	10	bar
32	1	0	0	0	1,8	2,9	4,4
40	1 1/4	0	0	1,8	2,3	3,7	5,5		Dext =	40	mm	Dext =	40	mm
50	1 1/2	0	1,8	2,0	2,9	4,6	6,9		s =	3,70	mm	s =	3,70	mm
63	2	1,8	2,0	2,5	3,6	5,8	8,6		Din =	32,6	mm	Din =	32,6	mm
75	2 1/2	1,9	2,3	2,9	4,3	6,8	10,3
90	3	2,2	2,8	3,5	5,1	8,2	12,3
110	4	2,7	3,4	4,2	6,3	10,0	15,1
125	5	3,1	3,9	4,8	7,1	11,4	17,1
140	5 1/2	3,5	4,3	5,4	8,0	12,7	19,2
160	6	4,0	4,9	6,2	9,1	14,6	21,9
180	7	4,4	5,5	6,9	10,2	16,4	24,6
200	8	4,9	6,2	7,7	11,4	18,2	27,4		Note (*)
225	9	5,5	6,9	8,6	12,8	20,5	30,8		Nominal diameters in inches in
250	10	6,2	7,7	9,6	14,2	22,7	34,2		red colour are not defined in the
280	11	6,9	8,6	10,7	15,9	25,4	38,3		imperial denomination
315	12	7,7	9,7	12,1	17,9	28,6	43,1
355	14	8,7	10,9	13,6	20,1	32,2	48,5
400	16	9,8	12,3	15,3	22,7	36,3	54,7
450	18	11,0	13,8	17,2	25,5	40,9	61,5
500	20	12,3	15,3	19,1	28,4	45,4	68,3
560	22	13,7	17,2	21,4	31,7	50,8	0
630	24	15,4	19,3	24,1	35,7	57,2	0
710	28	17,4	21,8	27,2	40,2	64,5	0
800	32	19,6	24,5	30,6	45,3	0	0
900	36	22,0	27,6	34,4	51,0	0	0
1000	40	24,5	30,6	38,2	56,7	0	0
1100	0	26,9	33,7	42,0	62,4	0	0
1200	48	29,4	36,7	45,9	68,0	0	0
1400	54	34,4	42,9	53,5	0	0	0
1600	64	39,2	49,0	61,2	0	0	0

						ISO 4427 PE 80 Design stress 6.3 MPa