## 1.CS
6	10,3	1,73	2,41	-	-	-	-	1,73	-	2,41	-	-	-	-
8	13,7	2,24	3,02	-	-	-	-	2,24	-	3,02	-	-	-	-		Application			Dn =	8	mm
10	17,1	2,31	3,2	-	-	-	-	2,31	-	3,2	-	-	-	-		(with input validation)			SCH =	40
15	21,3	2,77	3,73	7,47	-	-	-	2,77	-	3,73	-	-	-	4,78		di =	Pipe_CS_Dint_dn_sch =			#NAME?	mm
20	26,7	2,87	3,91	7,82	-	-	-	2,87	-	3,91	-	-	-	5,56		de =	Pipe_CS_Dext_dn =			#NAME?	mm
25	33,4	3,38	4,55	9,09	-	-	-	3,38	-	4,55	-	-	-	6,35		s =	Pipe_CS_Thickness_dn_sch =			#NAME?	mm
32	42,2	3,56	4,85	9,7	-	-	-	3,56	-	4,85	-	-	-	6,35
40	48,3	3,68	5,08	10,15	-	-	-	3,68	-	5,08	-	-	-	7,14
50	60,3	3,91	5,54	11,07	-	-	-	3,91	-	5,54	-	-	-	8,74
65	73	5,16	7,01	14,02	-	-	-	5,16	-	7,01	-	-	-	9,53		Application			Dn =	350	mm
80	88,9	5,49	7,62	15,24	-	-	-	5,49	-	7,62	-	-	-	11,13		(without input validation)			SCH =	40
90	101,6	5,74	8,08	-	-	-	-	5,74	-	8,08	-	-	-	-		di =	Pipe_CS_Dint_dn_sch =			333,34	mm
100	114,3	6,02	8,56	17,12	-	-	-	6,02	-	8,56	-	11,13	-	13,49		de =	Pipe_CS_Dext_dn =			355,6	mm
125	141,3	6,55	9,53	19,05	-	-	-	6,55	-	9,53	-	12,7	-	15,88		s =	Pipe_CS_Thickness_dn_sch =			11,13	mm
150	168,3	7,11	10,97	21,95	-	-	-	7,11	-	10,97	-	14,27	-	18,26		The shedule entered is wrong
200	219,1	8,18	12,7	22,23	-	6,35	7,04	8,18	10,31	12,7	15,09	18,26	20,62	23,01
250	273,1	9,27	12,7	25,4	-	6,35	7,8	9,27	12,7	15,09	18,26	21,44	25,4	28,58
300	323,9	9,53	12,7	25,4	-	6,35	8,38	10,31	14,27	17,48	21,44	25,4	28,58	33,32
350	355,6	9,53	12,7	-	6,35	7,92	9,53	11,13	15,09	19,05	23,83	27,79	31,75	35,71
400	406,4	9,53	12,7	-	6,35	7,92	9,53	12,7	16,66	21,44	26,19	30,96	36,53	40,49
450	457	9,53	12,7	-	6,35	7,92	11,13	14,27	19,05	23,83	29,36	34,93	39,67	45,24
500	508	9,53	12,7	-	6,35	9,53	12,7	15,09	20,62	26,19	32,54	38,1	44,45	50,01
550	559	9,53	12,7	-	6,35	9,53	12,7	-	22,23	28,58	34,93	41,28	47,63	53,98
600	610	9,53	12,7	-	6,35	9,53	14,27	17,48	24,61	30,96	38,89	46,02	52,37	59,54
650	660	9,53	12,7	-	7,92	12,7	-	-	-	-	-	-	-	-
700	711	9,53	12,7	-	7,92	12,7	15,88	-	-	-	-	-	-	-
750	762	9,53	12,7	-	7,92	12,7	15,88	-	-	-	-	-	-	-
800	813	9,53	12,7	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-
850	864	9,53	12,7	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-
900	914	9,53	12,7	-	7,92	12,7	15,88	19,05	-	-	-	-	-	-
1050	1067	9,53	12,7	-	-	-	-	-	-	-	-	-
		STD	ExStr	XxStr	10	20	30	40	60	80	100	120	140	160

AC
6	STD
8	ExStr
10	XxStr
15	10
20	20
25	30
32	40
40	60
50	80
65	100
80	120
90	140
100	160
125
150
200
250
300
350
400
450
500
550
600
650
700
750
800
850
900
1050

## 2.SS
6	10,29	-	1,24	1,73	2,41
8	13,72	-	1,65	2,24	3,02		Application			Dn =	350	mm
10	17,15	-	1,65	2,31	3,2		(with input validation)			SCH =	10S
15	21,34	1,65	2,11	2,77	3,73		di =	Pipe_SS_Dint_dn_sch =			#NAME?	mm
20	26,67	1,65	2,11	2,87	3,91		de =	Pipe_SS_Dext_dn =			#NAME?	mm
25	33,4	1,65	2,77	3,38	4,55		s =	Pipe_SS_Thickness_dn_sch =			#NAME?	mm
32	42,16	1,65	2,77	3,56	4,85
40	48,26	1,65	2,77	3,68	5,08			Pipe_SS_Dext_dn			#NAME?
50	60,33	1,65	2,77	3,91	5,54
65	73,03	2,11	3,05	5,16	7,01		Application			Dn =	350	mm
80	88,9	2,11	3,05	5,49	7,62		(without input validation)			SCH =	10S
100	114,3	2,11	3,05	6,02	8,56		di =	Pipe_SS_Dint_dn_sch =			346,04	mm
125	141,3	2,77	3,4	6,55	9,52		de =	Pipe_SS_Dext_dn =			355,6	mm
150	168,28	2,77	3,4	7,11	10,97		s =	Pipe_SS_Thickness_dn_sch =			4,78	mm
200	219,08	2,77	3,76	8,18	12,7		The shedule entered is wrong
250	273,05	3,4	4,19	9,27	12,7
300	323,85	3,96	4,57	9,52	12,7
350	355,6	3,96	4,78	-	-
400	406,4	4,19	4,78	-	-
450	457,2	4,19	4,78	-	-
500	508	4,78	5,54	-	-
600	609,6	5,54	6,35	-	-
750	762	6,35	7,92	-	-
NOMINAL / SIZE (DN)	OUTSIDE / DIAM.	5S	10S	40S	80S
		WALL THICKNESS (mm)
STAINLESS STEEL PIPES TO AMERICAN STANDARD ASME B36.19					From Onesteel

2.- Stainless steel pipes
dn	Sch
mm	-
6	5S
8	10S
10	40S
15	80S
20
25
32
40
50
65
80
100
125
150
200
250
300
350
400
450
500
600
750

## 3.HDPE_PE100
16					2,3
20					2,3		Application			Dn =	355	mm
25					2,3	2,8		(with input validation)			PN =	10
32					2,4	3	3,6		di =	Pipe_HDPE_PE100_Dint_Dn_PN(N2; N3)			312,8	mm
40				2,4	3	3,7	4,5		de =	Pipe_HDPE_PE100_Dext_Dn(N2)			355	mm
50			2,4	3	3,7	4,6	5,6		s =	Pipe_HDPE_PE100_Thickness_Dn_PN(N2; N3)			21,1	mm
63		2,3	3	3,8	4,7	5,8	7,1
75		2,8	3,6	4,5	5,6	6,8	8,4
90	2,3	3,3	4,3	5,4	6,7	8,2	10,1
110	2,7	4	5,3	6,6	8,1	10	12,3		Application			Dn =	355	mm
125	3,1	4,6	6	7,4	9,2	11,4	14		(without input validation)			PN =	10
140	3,5	5,1	6,7	8,3	10,3	12,7	15,7		di =	Pipe_HDPE_PE100_Dint_Dn_PN(N2; N3)			312,8	mm
160	4	5,8	7,7	9,5	11,8	14,6	17,9		de =	Pipe_HDPE_PE100_Dext_Dn(N2)			355	mm
180	4,4	6,6	8,6	10,7	13,3	16,4	20,1		s =	Pipe_HDPE_PE100_Thickness_Dn_PN(N2; N3)			21,1	mm
200	4,9	7,3	9,6	11,9	14,7	18,2	22,4		The nominal pressure entered is wrong
225	5,5	8,2	10,8	13,4	16,6	20,5	25,2
250	6,2	9,1	11,9	14,8	18,4	22,7	27,9
280	6,9	10,2	13,4	16,6	20,6	25,4	31,3
315	7,7	11,4	15	18,7	23,2	28,6	35,2
355	8,7	12,9	16,9	21,1	26,1	32,2	39,7
400	9,8	14,5	19,1	23,7	29,4	36,3	44,7
450	11	16,3	21,5	26,7	33,1	40,9	50,3
500	12,3	18,1	23,9	29,7	36,8	45,4	55,8
560	13,7	20,3	26,7	33,2	41,2	50,8
630	15,4	22,8	30	37,4	46,2	57,2
710	17,4	25,7	33,9	42,1	52,2
800	19,6	29	38,1	47,4	58,8
900	22	32,6	42,6	53,3
1000	24,5	36,2	47,7	59,3
1200	29,4	43,4	57,2
1400	34,3	50,6
1600	39,2	57,9
Dn [mm]	4	6	8	10	12,5	16	20
	Presiones nominales PN [bar]
HDPE PE100

dn	PN
mm	bar
16	4
20	6
25	8
32	10
40	12,5
50	16
63	20
75
90
110
125
140
160
180
200
225
250
280
315
355
400
450
500
560
630
710
800
900
1000
1200
1400
1600

	http://www.vinilit.cl/pdf_2/tub_fittings_hdpe_min.pdf					http://www.vinilit.cl/pdf_2/tub_fittings_hdpe_min.pdf

## 4.HDPE_PE80
16					2,2	1
20					1,9	2,8	2		Application			Dn =	355	mm
25					2,3	3,5	3		(with input validation)			PN =	10
32				1,8	2,9	4,4	4		di =	Pipe_HDPE_PE80_Dint_Dn_PN(N2,N3)			290,6	mm
40			1,8	2,3	3,7	5,5	5		de =	Pipe_HDPE_PE80_Dext_Dn(N2)			355	mm
50		1,8	2,0	2,9	4,6	6,9	6		s =	Pipe_HDPE_PE80_Thickness_Dn_PN(N2,N3)			32,2	mm
63	1,8	2,0	2,5	3,6	5,8	8,6	7
75	1,9	2,3	2,9	4,3	6,8	10,3	8
90	2,2	2,8	3,5	5,1	8,2	12,3	9
110	2,7	3,4	4,2	6,3	10,0	15,1	10		Application			Dn =	355	mm
125	3,1	3,9	4,8	7,1	11,4	17,1	11		(without input validation)			PN =	11
140	3,5	4,3	5,4	8,0	12,7	19,2	12		di =	Pipe_HDPE_PE80_Dint_Dn_PN			N/A	mm
160	4,0	4,9	6,2	9,1	14,6	21,9	13		de =	Pipe_CS_Dext_dn			355	mm
180	4,4	5,5	6,9	10,2	16,4	24,6	14		s =	Pipe_HDPE_PE100_Thickness_Dn_PN			N/A	mm
200	4,9	6,2	7,7	11,4	18,2	27,4	15		The nominal pressure entered is wrong
225	5,5	6,9	8,6	12,8	20,5	30,8	16
250	6,2	7,7	9,6	14,2	22,7	34,2	17
280	6,9	8,6	10,7	15,9	25,4	38,3	18		Application with imput diameter in imperial units
315	7,7	9,7	12,1	17,9	28,6	43,1	19
355	8,7	10,9	13,6	20,1	32,2	48,5	20		Application			Dn =	14	in
400	9,8	12,3	15,3	22,7	36,3	54,7	21		(without input validation)			PN =	10
450	11,0	13,8	17,2	25,5	40,9	61,5	22		di =	Pipe_Imp_HDPE_PE80_Dint_Dn_PN(N2,N3)			290,6	mm
500	12,3	15,3	19,1	28,4	45,4	68,3	23		de =	Pipe_Imp_HDPE_PE80_Dext_Dn(N2)			355	mm
560	13,7	17,2	21,4	31,7	50,8		24		s =	Pipe_Imp_HDPE_PE80_Thickness_Dn_PN(N2,N3)			32,2	mm
630	15,4	19,3	24,1	35,7	57,2		25
710	17,4	21,8	27,2	40,2	64,5		26
800	19,6	24,5	30,6	45,3			27
900	22,0	27,6	34,4	51,0			28
1000	24,5	30,6	38,2	56,7			29
1100	26,9	33,7	42,0	62,4			30
1200	29,4	36,7	45,9	68,0			31
1400	34,4	42,9	53,5				32
1600	39,2	49,0	61,2				33
Dn [mm]	2 1/2	3,2	4	6	10	16
	Presiones nominales PN [bar]
	HDPE PE80 DIN 8074 / ISO 4427
Espesor [mm]
1	2	3	4	5	6	7

HDPE 80 DIN 8074
dn	PN
mm	bar
16	2,5
20	3,2
25	4
32	6
40	10
50	16
63
75
90
110
125
140
160
180
200
225
250
280
315
355
400
450
500
560
630
710
800
900
1000
1100
1200
1400
1600

## 1.CS_2
6	10,3	1,73	2,41	-	-	-	-	1,73	-	2,41	-	-	-	-
8	13,7	2,24	3,02	-	-	-	-	2,24	-	3,02	-	-	-	-		Application			Dn =	8	mm
10	17,1	2,31	3,2	-	-	-	-	2,31	-	3,2	-	-	-	-		(with input validation)			SCH =	40
15	21,3	2,77	3,73	7,47	-	-	-	2,77	-	3,73	-	-	-	4,78		di =	Pipe_CS_Dint_dn_sch =			#NAME?	mm
20	26,7	2,87	3,91	7,82	-	-	-	2,87	-	3,91	-	-	-	5,56		de =	Pipe_CS_Dext_dn =			#NAME?	mm
25	33,4	3,38	4,55	9,09	-	-	-	3,38	-	4,55	-	-	-	6,35		s =	Pipe_CS_Thickness_dn_sch =			#NAME?	mm
32	42,2	3,56	4,85	9,7	-	-	-	3,56	-	4,85	-	-	-	6,35
40	48,3	3,68	5,08	10,15	-	-	-	3,68	-	5,08	-	-	-	7,14
50	60,3	3,91	5,54	11,07	-	-	-	3,91	-	5,54	-	-	-	8,74
65	73	5,16	7,01	14,02	-	-	-	5,16	-	7,01	-	-	-	9,53		Application			Dn =	350	mm
80	88,9	5,49	7,62	15,24	-	-	-	5,49	-	7,62	-	-	-	11,13		(without input validation)			SCH =	40
90	101,6	5,74	8,08	-	-	-	-	5,74	-	8,08	-	-	-	-		di =	Pipe_CS_Dint_dn_sch =			333,34	mm
100	114,3	6,02	8,56	17,12	-	-	-	6,02	-	8,56	-	11,13	-	13,49		de =	Pipe_CS_Dext_dn =			355,6	mm
125	141,3	6,55	9,53	19,05	-	-	-	6,55	-	9,53	-	12,7	-	15,88		s =	Pipe_CS_Thickness_dn_sch =			11,13	mm
150	168,3	7,11	10,97	21,95	-	-	-	7,11	-	10,97	-	14,27	-	18,26		The shedule entered is wrong
200	219,1	8,18	12,7	22,23	-	6,35	7,04	8,18	10,31	12,7	15,09	18,26	20,62	23,01
250	273,1	9,27	12,7	25,4	-	6,35	7,8	9,27	12,7	15,09	18,26	21,44	25,4	28,58
300	323,9	9,53	12,7	25,4	-	6,35	8,38	10,31	14,27	17,48	21,44	25,4	28,58	33,32
350	355,6	9,53	12,7	-	6,35	7,92	9,53	11,13	15,09	19,05	23,83	27,79	31,75	35,71
400	406,4	9,53	12,7	-	6,35	7,92	9,53	12,7	16,66	21,44	26,19	30,96	36,53	40,49
450	457	9,53	12,7	-	6,35	7,92	11,13	14,27	19,05	23,83	29,36	34,93	39,67	45,24
500	508	9,53	12,7	-	6,35	9,53	12,7	15,09	20,62	26,19	32,54	38,1	44,45	50,01
550	559	9,53	12,7	-	6,35	9,53	12,7	-	22,23	28,58	34,93	41,28	47,63	53,98
600	610	9,53	12,7	-	6,35	9,53	14,27	17,48	24,61	30,96	38,89	46,02	52,37	59,54
650	660	9,53	12,7	-	7,92	12,7	-	-	-	-	-	-	-	-
700	711	9,53	12,7	-	7,92	12,7	15,88	-	-	-	-	-	-	-
750	762	9,53	12,7	-	7,92	12,7	15,88	-	-	-	-	-	-	-
800	813	9,53	12,7	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-
850	864	9,53	12,7	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-
900	914	9,53	12,7	-	7,92	12,7	15,88	19,05	-	-	-	-	-	-
1050	1067	9,53	12,7	-	-	-	-	-	-	-	-	-
		STD	ExStr	XxStr	10	20	30	40	60	80	100	120	140	160

AC
6	STD
8	ExStr
10	XxStr
15	10
20	20
25	30
32	40
40	60
50	80
65	100
80	120
90	140
100	160
125
150
200
250
300
350
400
450
500
550
600
650
700
750
800
850
900
1050

## 4.HDPE_PE100_2
16					2,3
20					2,3		Application			Dn =	355	mm
25					2,3	2,8		(with input validation)			PN =	10
32					2,4	3	3,6		di =	Pipe_HDPE_PE100_Dint_Dn_PN(N2; N3)			312,8	mm
40				2,4	3	3,7	4,5		de =	Pipe_HDPE_PE100_Dext_Dn(N2)			355	mm
50			2,4	3	3,7	4,6	5,6		s =	Pipe_HDPE_PE100_Thickness_Dn_PN(N2; N3)			21,1	mm
63		2,3	3	3,8	4,7	5,8	7,1
75		2,8	3,6	4,5	5,6	6,8	8,4
90	2,3	3,3	4,3	5,4	6,7	8,2	10,1
110	2,7	4	5,3	6,6	8,1	10	12,3		Application			Dn =	355	mm
125	3,1	4,6	6	7,4	9,2	11,4	14		(without input validation)			PN =	10
140	3,5	5,1	6,7	8,3	10,3	12,7	15,7		di =	Pipe_HDPE_PE100_Dint_Dn_PN(N2; N3)			312,8	mm
160	4	5,8	7,7	9,5	11,8	14,6	17,9		de =	Pipe_HDPE_PE100_Dext_Dn(N2)			355	mm
180	4,4	6,6	8,6	10,7	13,3	16,4	20,1		s =	Pipe_HDPE_PE100_Thickness_Dn_PN(N2; N3)			21,1	mm
200	4,9	7,3	9,6	11,9	14,7	18,2	22,4		The nominal pressure entered is wrong
225	5,5	8,2	10,8	13,4	16,6	20,5	25,2
250	6,2	9,1	11,9	14,8	18,4	22,7	27,9
280	6,9	10,2	13,4	16,6	20,6	25,4	31,3
315	7,7	11,4	15	18,7	23,2	28,6	35,2
355	8,7	12,9	16,9	21,1	26,1	32,2	39,7
400	9,8	14,5	19,1	23,7	29,4	36,3	44,7
450	11	16,3	21,5	26,7	33,1	40,9	50,3
500	12,3	18,1	23,9	29,7	36,8	45,4	55,8
560	13,7	20,3	26,7	33,2	41,2	50,8
630	15,4	22,8	30	37,4	46,2	57,2
710	17,4	25,7	33,9	42,1	52,2
800	19,6	29	38,1	47,4	58,8
900	22	32,6	42,6	53,3
1000	24,5	36,2	47,7	59,3
1200	29,4	43,4	57,2
1400	34,3	50,6
1600	39,2	57,9
Dn [mm]	4	6	8	10	12,5	16	20
	Presiones nominales PN [bar]
HDPE PE100

dn	PN
mm	bar
16	4
20	6
25	8
32	10
40	12,5
50	16
63	20
75
90
110
125
140
160
180
200
225
250
280
315
355
400
450
500
560
630
710
800
900
1000
1200
1400
1600

	http://www.vinilit.cl/pdf_2/tub_fittings_hdpe_min.pdf					http://www.vinilit.cl/pdf_2/tub_fittings_hdpe_min.pdf

## 4.HDPE_PE80_2
16					2,2	1
20					1,9	2,8	2		Application			Dn =	355	mm
25					2,3	3,5	3		(with input validation)			PN =	10
32				1,8	2,9	4,4	4		di =	Pipe_HDPE_PE80_Dint_Dn_PN(N2,N3)			290,6	mm
40			1,8	2,3	3,7	5,5	5		de =	Pipe_HDPE_PE80_Dext_Dn(N2)			355	mm
50		1,8	2,0	2,9	4,6	6,9	6		s =	Pipe_HDPE_PE80_Thickness_Dn_PN(N2,N3)			32,2	mm
63	1,8	2,0	2,5	3,6	5,8	8,6	7
75	1,9	2,3	2,9	4,3	6,8	10,3	8
90	2,2	2,8	3,5	5,1	8,2	12,3	9
110	2,7	3,4	4,2	6,3	10,0	15,1	10		Application			Dn =	355	mm
125	3,1	3,9	4,8	7,1	11,4	17,1	11		(without input validation)			PN =	11
140	3,5	4,3	5,4	8,0	12,7	19,2	12		di =	Pipe_HDPE_PE80_Dint_Dn_PN			N/A	mm
160	4,0	4,9	6,2	9,1	14,6	21,9	13		de =	Pipe_CS_Dext_dn			355	mm
180	4,4	5,5	6,9	10,2	16,4	24,6	14		s =	Pipe_HDPE_PE100_Thickness_Dn_PN			N/A	mm
200	4,9	6,2	7,7	11,4	18,2	27,4	15		The nominal pressure entered is wrong
225	5,5	6,9	8,6	12,8	20,5	30,8	16
250	6,2	7,7	9,6	14,2	22,7	34,2	17
280	6,9	8,6	10,7	15,9	25,4	38,3	18		Application with imput diameter in imperial units
315	7,7	9,7	12,1	17,9	28,6	43,1	19
355	8,7	10,9	13,6	20,1	32,2	48,5	20		Application			Dn =	14	in
400	9,8	12,3	15,3	22,7	36,3	54,7	21		(without input validation)			PN =	10
450	11,0	13,8	17,2	25,5	40,9	61,5	22		di =	Pipe_Imp_HDPE_PE80_Dint_Dn_PN(N2,N3)			290,6	mm
500	12,3	15,3	19,1	28,4	45,4	68,3	23		de =	Pipe_Imp_HDPE_PE80_Dext_Dn(N2)			355	mm
560	13,7	17,2	21,4	31,7	50,8		24		s =	Pipe_Imp_HDPE_PE80_Thickness_Dn_PN(N2,N3)			32,2	mm
630	15,4	19,3	24,1	35,7	57,2		25
710	17,4	21,8	27,2	40,2	64,5		26
800	19,6	24,5	30,6	45,3			27
900	22,0	27,6	34,4	51,0			28
1000	24,5	30,6	38,2	56,7			29
1100	26,9	33,7	42,0	62,4			30
1200	29,4	36,7	45,9	68,0			31
1400	34,4	42,9	53,5				32
1600	39,2	49,0	61,2				33
Dn [mm]	2 1/2	3,2	4	6	10	16
	Presiones nominales PN [bar]
	HDPE PE80 DIN 8074 / ISO 4427
Espesor [mm]
1	2	3	4	5	6	7

HDPE 80 DIN 8074
dn	PN
mm	bar
16	2,5
20	3,2
25	4
32	6
40	10
50	16
63
75
90
110
125
140
160
180
200
225
250
280
315
355
400
450
500
560
630
710
800
900
1000
1100
1200
1400
1600

## 6.CS_Imp_2
1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17
2
3	Pipe Thickness [mm], according ASME B36.10M
4
5							ASME B36.10M SCHEDULE / IDENTIFICATION											Application			Dn =	10	in
6	Size	dext	5	10	20	30	40	60	80	100	120	140	160	STD	XS	XXS		(with input validation)			SCH =	XXS	-
7	1/2	21,3	1,65	2,11	-	2,41	2,77	-	3,73	-	0	-	4,78	2,77	3,73	7,47		di =	Pipe_Imp_CS_Dint_dn_sch			N/A	mm
8	3/4	26,7	1,65	2,11	-	2,41	2,87	-	3,91	-	0	-	5,56	2,87	3,91	7,82		de =	Pipe_Imp_CS_Dext_dn			406,4	mm
9	1	33,4	1,65	2,77	-	2,9	3,38	-	4,55	-	0	-	6,35	3,38	4,55	9,09		s =	Pipe_Imp_CS_Thickness_dn_sch			N/A	mm
10	1 1/4	42,2	1,65	2,77		2,97	3,56		4,85				6,35	3,56	4,85	9,7
11	1 1/2	48,3	1,65	2,77	-	3,18	3,68	-	5,08	-	0	-	7,14	3,68	5,08	10,15
12	2	60,3	1,65	2,77	-	3,18	3,91	-	5,54	-	0	-	8,74	3,91	5,54	11,07		Application			Dn =	16	in
13	2 1/2	73	2,11	3,05		4,78	5,16		7,01				9,53	5,16	7,01	14,02
14	3	88,9	2,11	3,05	-	4,78	5,49	-	7,62	-	0	-	11,13	5,49	7,62	15,24		(without input validation)			SCH =	81
15	3 1/2	101,6	2,11	3,05		4,78	5,74		8,08					5,74	8,08
16	4	114,3	2,11	3,05	-	4,78	6,02	-	8,56	-	11,13	-	13,49	6,02	8,56	17,12		di =	Pipe_Imp_CS_Dint_dn_sch			N/A	mm
17	5	141,3	2,77	3,4	-	-	6,55	-	9,53	-	12,7	-	15,88	6,55	9,53	19,05		de =	Pipe_Imp_CS_Dext_dn			559	mm
18	6	168,3	2,77	3,4	-	-	7,11	-	10,97	-	14,27	-	18,26	7,11	10,97	21,95		s =	Pipe_Imp_CS_Thickness_dn_sch			N/A	mm
19	8	219,1	2,77	3,76	6,35	7,04	8,18	10,31	12,7	15,09	18,26	20,62	23,01	8,18	12,7	22,23		The shedule entered is wrong
20	10	273	3,4	4,19	6,35	7,8	9,27	12,7	15,09	18,26	21,44	25,4	28,58	9,27	12,7	25,4
21	12	323,8	3,96	4,57	6,35	8,38	10,31	14,27	17,48	21,44	25,4	28,58	33,32	9,53	12,7	25,4
22	14	355,6	3,96	6,35	7,92	9,53	11,13	15,09	19,05	23,83	27,79	31,75	35,71	9,53	12,7	-
23	16	406,4	4,19	6,35	7,92	9,53	12,7	16,66	21,44	26,19	30,96	36,53	40,49	9,53	12,7	-
24	18	457	4,19	6,35	7,92	11,13	14,27	19,05	23,83	29,36	34,93	39,67	45,24	9,53	12,7	-
25	20	508	4,78	6,35	9,53	12,7	15,09	20,62	26,19	32,54	38,1	44,45	50,01	9,53	12,7	-
26	22	559	4,78	6,35	9,53	12,7	-	22,23	28,58	34,93	41,28	47,63	53,98	9,53	12,7	-
27	24	610	5,54	6,35	9,53	14,27	17,48	24,61	30,96	38,89	46,02	52,37	59,54	9,53	12,7	-
28	26	660	-	7,92	12,7	15,88	-	-	-	-	-	-	-	9,53	12,7	-
29	28	711	-	7,92	12,7	-	-	-	-	-	-	-	-	9,53	12,7	-
30	30	762	6,35	7,92	12,7	15,88	-	-	-	-	-	-	-	9,53	12,7	-
31	32	813	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-	9,53	12,7	-
32	34	864	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-	9,53	12,7	-
33	36	914	-	7,92	12,7	15,88	19,05	-	-	-	-	-	-	9,53	12,7	-
34	38	965	-	-	-	-	-	-	-	-	-	9,53	12,7	-
35	40	1016	-	-	-	-	-	-	-	-	-	9,53	12,7	-
36	42	1067	-	-	-	-	-	-	-	-	-	9,53	12,7	-
	44	1118	-	-	-	-	-	-	-	-	-	9,53	12,7	-
	46	1168	-	-	-	-	-	-	-	-	-	9,53	12,7	-
39	48	1219	-	-	-	-	-	-	-	-	-	9,53	12,7	-

	Carbon steel pipes
	dn	Sc -
	in
	1/2	5
	3/4	10
	1	20
	1 1/2	30
	2	40
	3	60
	4	80
	5	100
	6	120
	8	140
	10	160
	12	STD
	14	XS
	16	XXS
	18
	20
	22
	24
	26
	28
	30
	32
	34
	36
	38
	40
	42
	44
	46
	48

## 6.CS_Imp
1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17
2
3	Pipe Thickness [mm], according ASME B36.10M
4
5							ASME B36.10M SCHEDULE / IDENTIFICATION											Application			Dn =	10	in
6	Size	dext	5	10	20	30	40	60	80	100	120	140	160	STD	XS	XXS		(with input validation)			SCH =	XXS	-
7	1/2	21,3	1,65	2,11	-	2,41	2,77	-	3,73	-	0	-	4,78	2,77	3,73	7,47		di =	Pipe_Imp_CS_Dint_dn_sch			N/A	mm
8	3/4	26,7	1,65	2,11	-	2,41	2,87	-	3,91	-	0	-	5,56	2,87	3,91	7,82		de =	Pipe_Imp_CS_Dext_dn			406,4	mm
9	1	33,4	1,65	2,77	-	2,9	3,38	-	4,55	-	0	-	6,35	3,38	4,55	9,09		s =	Pipe_Imp_CS_Thickness_dn_sch			N/A	mm
10	1 1/4	42,2	1,65	2,77		2,97	3,56		4,85				6,35	3,56	4,85	9,7
11	1 1/2	48,3	1,65	2,77	-	3,18	3,68	-	5,08	-	0	-	7,14	3,68	5,08	10,15
12	2	60,3	1,65	2,77	-	3,18	3,91	-	5,54	-	0	-	8,74	3,91	5,54	11,07		Application			Dn =	16	in
13	2 1/2	73	2,11	3,05		4,78	5,16		7,01				9,53	5,16	7,01	14,02
14	3	88,9	2,11	3,05	-	4,78	5,49	-	7,62	-	0	-	11,13	5,49	7,62	15,24		(without input validation)			SCH =	81
15	3 1/2	101,6	2,11	3,05		4,78	5,74		8,08					5,74	8,08
16	4	114,3	2,11	3,05	-	4,78	6,02	-	8,56	-	11,13	-	13,49	6,02	8,56	17,12		di =	Pipe_Imp_CS_Dint_dn_sch			N/A	mm
17	5	141,3	2,77	3,4	-	-	6,55	-	9,53	-	12,7	-	15,88	6,55	9,53	19,05		de =	Pipe_Imp_CS_Dext_dn			559	mm
18	6	168,3	2,77	3,4	-	-	7,11	-	10,97	-	14,27	-	18,26	7,11	10,97	21,95		s =	Pipe_Imp_CS_Thickness_dn_sch			N/A	mm
19	8	219,1	2,77	3,76	6,35	7,04	8,18	10,31	12,7	15,09	18,26	20,62	23,01	8,18	12,7	22,23		The shedule entered is wrong
20	10	273	3,4	4,19	6,35	7,8	9,27	12,7	15,09	18,26	21,44	25,4	28,58	9,27	12,7	25,4
21	12	323,8	3,96	4,57	6,35	8,38	10,31	14,27	17,48	21,44	25,4	28,58	33,32	9,53	12,7	25,4
22	14	355,6	3,96	6,35	7,92	9,53	11,13	15,09	19,05	23,83	27,79	31,75	35,71	9,53	12,7	-
23	16	406,4	4,19	6,35	7,92	9,53	12,7	16,66	21,44	26,19	30,96	36,53	40,49	9,53	12,7	-
24	18	457	4,19	6,35	7,92	11,13	14,27	19,05	23,83	29,36	34,93	39,67	45,24	9,53	12,7	-
25	20	508	4,78	6,35	9,53	12,7	15,09	20,62	26,19	32,54	38,1	44,45	50,01	9,53	12,7	-
26	22	559	4,78	6,35	9,53	12,7	-	22,23	28,58	34,93	41,28	47,63	53,98	9,53	12,7	-
27	24	610	5,54	6,35	9,53	14,27	17,48	24,61	30,96	38,89	46,02	52,37	59,54	9,53	12,7	-
28	26	660	-	7,92	12,7	15,88	-	-	-	-	-	-	-	9,53	12,7	-
29	28	711	-	7,92	12,7	-	-	-	-	-	-	-	-	9,53	12,7	-
30	30	762	6,35	7,92	12,7	15,88	-	-	-	-	-	-	-	9,53	12,7	-
31	32	813	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-	9,53	12,7	-
32	34	864	-	7,92	12,7	15,88	17,48	-	-	-	-	-	-	9,53	12,7	-
33	36	914	-	7,92	12,7	15,88	19,05	-	-	-	-	-	-	9,53	12,7	-
34	38	965	-	-	-	-	-	-	-	-	-	9,53	12,7	-
35	40	1016	-	-	-	-	-	-	-	-	-	9,53	12,7	-
36	42	1067	-	-	-	-	-	-	-	-	-	9,53	12,7	-
	44	1118	-	-	-	-	-	-	-	-	-	9,53	12,7	-
	46	1168	-	-	-	-	-	-	-	-	-	9,53	12,7	-
39	48	1219	-	-	-	-	-	-	-	-	-	9,53	12,7	-

	Carbon steel pipes
	dn	Sc -
	in
	1/2	5
	3/4	10
	1	20
	1 1/2	30
	2	40
	3	60
	4	80
	5	100
	6	120
	8	140
	10	160
	12	STD
	14	XS
	16	XXS
	18
	20
	22
	24
	26
	28
	30
	32
	34
	36
	38
	40
	42
	44
	46
	48

## 7.SS_Imp
NOMINAL SIZE	NOMINAL O.D	5S	10S	40S	80S
	mm	di [mm]	di [mm]	di [mm]	di [mm]
Stainless Steel Pipe Schedule
ANSI B36.10
dn	de	Internal diameter [mm]						Application			Dn =	1,5	in
1/8	10,29	-	7,81	6,83	5,47			(with input validation)			SCH =	5S
1/4	13,72	-	10,42	9,24	7,68			di =	Pipe_Imp_SS_Dint_Dn_SCH			44,96	mm
3/8	17,15	-	13,85	12,53	10,75			de =	Pipe_Imp_SS_Dext_Dn			48,26	mm
1/2	21,34	18,04	17,12	15,80	13,88			s =	Pipe_Imp_SS_Thickness_Dn_SCH			1,65	mm
3/4	26,67	23,37	22,45	20,93	18,85
1	33,40	30,10	27,86	26,64	24,30
1 1/4	42,16	38,86	36,62	35,04	32,46			Application			Dn =	1,5	in
1 1/2	48,26	44,96	42,72	40,90	38,10			(without input validation)			SCH =	5S
2	60,33	57,03	54,79	52,51	49,25			di =	Pipe_Imp_SS_Dint_Dn_SCH			44,96	mm
2 1/2	73,03	68,81	66,93	62,71	59,01			de =	Pipe_Imp_SS_Dext_Dn			48,26	mm
3	88,90	84,68	82,80	77,92	73,66			s =	Pipe_Imp_SS_Thickness_Dn_SCH			1,65	mm
3 1/2	101,60	97,38	95,50	90,12	85,44			The nominal diameter entered is wrong
4	114,30	110,08	108,20	102,26	97,18
5	141,30	135,76	134,50	128,20	122,24
6	168,28	162,74	161,48	154,06	146,34
8	219,08	213,54	211,56	202,72	193,68
10	273,05	266,25	264,67	254,51	247,65
12	323,85	315,93	314,71	304,79	298,45
14	355,60	347,68	346,04	-	-
16	406,40	398,02	396,84	-	-
18	457,20	448,82	447,64	-	-
20	508,00	498,44	496,91	-	-
22	558,80	549,24	547,72	-	-
24	609,60	598,52	596,90	-	-
30	762,00	749,30	746,16	-	-

							Note 1

dn	Sch
in	-
1/8	5S
1/4	10S
3/8	40S
1/2	80S
3/4
1
1 1/4
1 1/2
2
2 1/2
3
3 1/2
4
5
6
8
10
12
14
16
18
20
22
24
30

## Water Data
0	0,569	4,217	12,99	1000,00	1,75E-03	1,75E-06	1,35E-07	0,0061
1,85000000000002	0,574	4,211	12,22	1000,00	1,65E-03	1,65E-06	1,36E-07	0,0070		Application example
6,85000000000002	0,582	4,198	10,26	1000,00	1,42E-03	1,42E-06	1,39E-07	0,0099
11,85	0,590	4,189	8,81	1000,00	1,23E-03	1,23E-06	1,41E-07	0,0139		Input data: Temperature			t =	35	ºC
16,85	0,598	4,184	7,56	999,00	1,08E-03	1,08E-06	1,43E-07	0,0192
21,85	0,606	4,181	6,62	998,00	9,59E-04	9,61E-07	1,45E-07	0,0262		Function used				Results
26,85	0,613	4,179	5,83	997,01	8,55E-04	8,58E-07	1,47E-07	0,0353		SaturatedWaterConductivity_t			k =	Err:502	W/(m*K)
31,85	0,620	4,178	5,2	995,02	7,69E-04	7,73E-07	1,49E-07	0,0471		SaturatedWaterSpecificHeat_t			Cp =	Err:502	kJ/kg
36,85	0,628	4,178	4,62	993,05	6,95E-04	7,00E-07	1,51E-07	0,0622		SaturatedWaterPrandtl_t			Pr =	Err:502	-
41,85	0,634	4,179	4,16	991,08	6,31E-04	6,37E-07	1,53E-07	0,0813		SaturatedWaterDensity_t			r =	Err:502	kg/m3
46,85	0,640	4,18	3,77	989,12	5,77E-04	5,78E-07	1,53E-07	0,1053		SaturatedWaterAbsoluteViscosity_t			m =	Err:502	Pa*s
51,85	0,645	4,182	3,42	987,17	5,28E-04	5,35E-07	1,56E-07	0,1351		SaturatedWaterKinematicViscosity_t			n =	Err:502	m2/s
56,85	0,651	4,184	3,15	984,25	4,89E-04	4,97E-07	1,58E-07	0,1719		SaturatedWaterThermalDiffusivity_t			a =	Err:502	m2/s
61,85	0,656	4,186	2,88	982,32	4,53E-04	4,61E-07	1,60E-07	0,2169
66,85	0,660	4,188	2,66	979,43	4,20E-04	4,29E-07	1,61E-07	0,2715
71,85	0,664	4,191	2,45	976,56	3,89E-04	3,98E-07	1,63E-07	0,3374
76,85	0,668	4,195	2,29	973,71	3,65E-04	3,75E-07	1,64E-07	0,4163
81,85	0,671	4,199	2,14	970,87	3,43E-04	3,53E-07	1,65E-07	0,5102
86,85	0,674	4,203	2,02	967,12	3,24E-04	3,35E-07	1,66E-07	0,6213
91,85	0,677	4,209	1,91	963,39	3,06E-04	3,18E-07	1,67E-07	0,7518
96,85	0,679	4,214	1,8	960,61	2,89E-04	3,01E-07	1,68E-07	0,9045
100	0,680	4,217	1,76	957,85	2,79E-04	2,91E-07	1,68E-07	1,0133

t	k	Cp	Pr	ragua	m	n	a	Psat
ºC	W/(m*K)	kJ/(kg*K)	-	kg/m3	Pa s	m2/s	m2/s	bar	K

Saturation properties of water as a function of the temperature

## Air Data
-73,15	0,0181	1,007	0,737	1,7458	1,325E-05
-23,15	0,0223	1,006	0,72	1,3947	1,596E-05		Application example
26,85	0,0263	1,007	0,707	1,1614	1,846E-05
76,85	0,03	1,009	0,7	0,995	2,082E-05		Input data: Temperature				t =	35	ºC
126,85	0,0338	1,014	0,69	0,8711	2,301E-05
176,85	0,0373	1,021	0,686	0,774	2,507E-05		Function used					Results
226,85	0,0407	1,03	0,684	0,6964	2,701E-05		AirConductivity_t(t)				k =	#NAME?	W/(m*K)
276,85	0,0439	1,04	0,683	0,6329	2,884E-05		AirSpecificHeat_t(t)				Cp =	#NAME?	kJ/kg
326,85	0,0469	1,051	0,685	0,5804	3,058E-05		AirPrandtl_t(t)				Pr =	#NAME?	-
376,85	0,0497	1,063	0,69	0,5356	3,225E-05		AirDensity_t(t)				r =	#NAME?	kg/m3
426,85	0,0524	1,075	0,695	0,4975	3,388E-05		AirAbsoluteViscosity				m =	#NAME?	Pa*s
476,85	0,0549	1,087	0,702	0,4643	3,546E-05		AirKinematicViscosity_t(t)				n =	#NAME?	m2/s
526,85	0,0573	1,099	0,709	0,4354	3,698E-05		AirThermalDiffusivity_t(t)				a =	#NAME?	m2/s
576,85	0,0596	1,11	0,716	0,4097	3,843E-05
626,85	0,062	1,121	0,72	0,3868	3,981E-05
676,85	0,0643	1,131	0,723	0,3666	4,113E-05
726,85	0,0667	1,141	0,726	0,3482	4,244E-05

t	k	Cp	Pr	ragua	m
ºC	W/(m*K)	kJ/(kg*K)	-	kg/m3	Pa s

Atmospheric air properties as a function of the temperature

## Re_HE
Re	1.000	10.000	100.000	1.000.000	He
100	0,420
200	0,140	0,6650
300	0,083	0,3195
400	0,056	0,1910
500	0,042	0,1387	0,9223
600	0,033	0,0944	0,6542
700	0,028	0,0720	0,4893
800	0,023	0,0587	0,3805
900	0,021	0,0491	0,3048
1.000	0,0184	0,0420	0,2499
2.000	0,0080	0,0143	0,0707	0,5499
3.000	0,0062	0,0080	0,0338	0,2506
4.000	0,0056	0,0062	0,0200	0,1435
5.000	0,0052	0,0057	0,0137	0,0931
6.000	0,0050	0,0056	0,0100	0,0654
7.000	0,0048	0,0054	0,0077	0,0485
8.000	0,0048	0,0053	0,0070	0,0374
9.000	0,0046	0,0051	0,0068	0,0298
10.000	0,0045	0,0050	0,0067	0,0243
20.000	0,0039	0,0044	0,0059	0,0083
30.000	0,0036	0,0040	0,0054	0,0063
40.000	0,0034	0,0038	0,0052	0,0056
50.000	0,0032	0,0036	0,0049	0,0054
60.000	0,0031	0,0035	0,0048	0,0052
70.000	0,0030	0,0034	0,0046	0,0050
80.000	0,0029	0,0034	0,0045	0,0049
90.000	0,0029	0,0033	0,0044	0,0047
100.000	0,0028	0,0032	0,0043	0,0046
200.000	0,0025	0,0028	0,0038	0,0040
300.000	0,0023	0,0026	0,0035	0,0037
400.000	0,0022	0,0025	0,0033	0,0035
500.000	0,0021	0,0024	0,0032	0,0033
600.000	0,0021	0,0023	0,0031	0,0032
700.000	0,0020	0,0022	0,0030	0,0031
800.000	0,0020	0,0022	0,0029	0,0030
900.000	0,0019	0,0021	0,0029	0,0030
1.000.000	0,0019	0,0021	0,0028	0,0029

## Index
				rev. Cjc. 10.07.2017

Flow rate and pressure loss

1. Manning equation					4. Channels
(usually applied for open channels)					Flow velocity in channels according Manning
The Maning equation relates the velocity of a fluid in an open channel, to					and Darcy-Weisbach
properties of the open channel.
It is presented a Darcy-Weisbach equation adapted to match the structure					5. Friction factors
of Manning's equation.					Visual Basic functions for:
This equation defines a Manning's coefficient that makes that the					- Serghides equation
Manning's equation is equivalent to the Darcy-Weisbach equation					- Swamee-Jain equation
				- Colebrook equation
1a. Manning application
Flow rate according Manning, using a calculated Manning coefficient					6. Colebrook
Result compared with tabulated Manning coefficient					Colebrook equations for Darcy-Weisbach and
				Fanning friction factors, using natural and decimal
2. Hazen Williams equation					logarithmus
(usually applied in potable water systems)
Hazen Williams empirical equation for friction head loss
The Hazen Williams equation was developed for water at temperatures normally
experienced in potable water systems, for pipe diameters d >= 50 mm and
within a moderate range of water velocity v <= 3 m/s.

3. Darcy					www.piping-tools.net
(analytical equation with an experimental coefficient)					Pipes. Flow rate and pressure loss equations.xls
Darcy-Weisbach equation for pressure loss					cjcruz@piping-tools.net
Deduction of equation

## 1. Application of slurry eqs.
				#REF!
				Page 1 of 4
Application of slurry properties equations

Input data				Inside pipe diameter (carbon steel)				Water density at termperature
Q =	0,018	m³/s		Di =	Pipe_Imp_CS_Dint_dn_sch			rw=	SaturatedWaterDensity_t
t =	10	°C		dn=	4	in		t =	10	ºC
rL=	1150	kg/m³		Sch =	STD	-		rw=	1.000	kg/m³
rs=	2800	kg/m³		Di =	102,3	mm
d50 =	16	mm					Specific gravity of solids
Cw =	30	%		Inside diameter				Ss =	rs / rw
Pipe mat =	CS	-		di =	Di -2* slining			rs=	2800	kg/m³
dn=	4	in		Di =	102,3	mm		rw=	1000	kg/m³
Sch =	STD	-		slining =	6	mm		Ss =	2,8	-
slining =	6	mm		di =	90,3	mm
Rabs =	0,1	mm		di =	0,0903	m		Specific gravity of Liquid
				SL =	rL / rw
For deduction of equations of slurry				Inside pipe area				rL=	1150	kg/m³
properties, see sheet 2				A =	(p/4)*di^2			rw=	1000	kg/m³
				di =	0,090	m		SL =	1,15	-
				A =	0,0064	m²

				Page 2 of 4
Volumetric concentration					Pulp density				Pulp specific gravity				Pulp to liquid density ratio

Volumetric concentration		Sheet 2, Eq. (o)		Volumetric concentration		Sheet Ref. 4, (2a)		Pulp density		Sheet 2. Eq. (u)		Pulp specific gravity				Pulp to liquid density ratio
				(Valid only if liquid is water		rL=rw)					Sp =	rp / rw			rP-L =	rp / rL	kg/m3
				rp=	1397	kg/m³		rp=	1397	kg/m³
				rw =	1000	kg/m3		rL =	1150	kg/m3
Cv =	Cw /(Cw + (1-Cw) * Ss/SL)					rp =	rL * (1-Cv) / (1-Cw)			Sp =	1,397	-		rP-L =	1,21	-
Cw =	0,30	-					rL =	1150	kg/m3
Ss =	2,80	-		Cv =	(Sp-1) / (Ss-1)			Cv =	0,1497	-
SL =	1,150			Sp =	1,239	-		Cw =	0,30	-
Cv =	0,150	-		Ss =	2,8 / -	-		rp =	1397	kg/m3
Cv =	15,0	%		Cv =	0,133	( if rL=rw)

Volumetric concentration		Sheet Ref. 2, (2.38a)

Cv =	Cw * rL / ( rs - Cw *(rs - rL ) )
Cw =	0,3	%
rs =	2800	kg/m3
rL =	1150	kg/m4
Cv =	0,150	-

				Page 3 of 4
Pulp dynamic viscosity				Pulp kinematic viscosity				Darcy-Weisbach friction factor				Mc Elvain and Cave correction factor				Specific heat of pulp

Viscosity ratio		[1], Eq. (1-9)		Pulp kinematic viscosity				Relative rugosity				Mc Elvain &Cave FL factor		Note (2)		Specific heat of pulp		Sheet Cp
(Pulp to water viscosity ratio)				np =	mp / rp			Rrel =	Rabs / di			(Visual Basic function)
mp/mw = 1 + K1 * (Cv /100) + K2 * (Cv/100)^2 +				mp =	2,1E-03	Pa s		Rabs =	0,1	mm		FL =	Slurry_Fl_McElvain_d50_Cv			Cpp =	Cw * Cps + (1-Cw)*Cpwater
	+ A * Exp(B*(Cv/100) )			rp =	1.397	kg/m3		di =	90,3	mm		d50 =	16	mm
[1] Eq. (1-9), page 1.22. Note (1)				np =	1,5E-06	m²/s		Rrel =	0,001			Cv =	14,97	%		Mas concentration of solid in pulp
Cv =	15,0	%					FL =	0,547	-		Cw =	0,30	-
K1 =	2,5					Reynolds					Specific heat of solids
K2 =	10,5			Flow velocity				Re =	v * di / n					Cps =	0,8	kJ/(kg*K)
A =	0,00273			v =	Q / A			v =	2,81	m/s					Specific heat of water
B =	16,6			Q =	0,018	m³/s		di =	0,0903	m					Cpwater =	4,184	kJ/(kg*K)
mp/mw =	1,64			A =	0,0064	m²		np =	1,5E-06	m²/s					Resulting specific heat of pulp
				v =	2,81	m/s		Re =	1,7E+05	-					Cpp =	3,17	kJ/(kg*K)
Dynamic viscosity of water
mw = SaturatedWaterAbsoluteViscosity_t(t)				Kinematic pressure				Darcy friction factor
t =	10	°C		hv =	(r/2) * v^2			(LO Calc Basic function)
mw =	1,3E-03	Pa s		rp =	1.397	kg/m3		f = Pipe_Friction_Factor_Rrel_Re
				v =	2,81	m/s		Rrel =	0,001	-
Pulp dynamic viscosity				hv =	5528	Pa		Re =	1,7E+05	-
mp =	ms/mw * mw					f =	0,022	-		Note (1)				Note (2)
mp/mw =	1,64					Thomas (1965) formula. Equation 1-9, [2] is widely				This correction factor is used for the calculation
mw =	1,3E-03	Pa s					accepted in the slurry industry for heterogeneous				of the limit deposition velocity. References from
mp =	2,1E-03	Pa s					mixtures of a Newtonian rheology.				JRI [4] are used for these calculations.
mp =	2,13	cP

				Page 4 of 4
Limit deposition velocity in pipes:
				The VBA function selects the appropiate function according
Application data			Applicabilty ranges					the particle diameter "d50" and pipe diameter "d".

d50 =	250	mm	10 mm < d50 < 3000 mm					For diameter input in inches and schedule standard
Cv =	35	%	5% <= Cv <= 40%					dn =	4	in
SS =	4,15	-					H9	VL =	Slurry_Limit_Deposition_Velocity_JRI_Imp_d50_Cv_dn_Ss
				VL =	2,79	m/s
H6
Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_hn_Ss					SI	channel		For diameter input in milimeters and schedule standard
				hn		dn =	100	mm
H7					H7	VL =	Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dn_Ss
Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dn_Ss					SI	Pipe		VL =	2,79	m/s
				dn
H8					For inside diameter input in milimeters
Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dinterior_Ss					SI	Pipe		d =	102	mm
				di	H8	VL =	SLURRY_LIMIT_DEPOSITION_VELOCITY_JRI_SI_D50_CV_DINTERIOR_SS
H9					VL =	2,79	m/s
Slurry_Limit_Deposition_Velocity_JRI_Imp_d50_Cv_dn_Ss					Imp	Pipe
				dn
H10
Slurry_Limit_Deposition_Velocity_Lining_JRI_Imp_d50_Cv_dn_Ss_Slining					Imp	Pipe		A resume of JRI equations is presented in sheet Ref. 4
				dn
				lining

' H6. Limit deposition velocity for channels, SI units
' Function Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_hn_Ss(d50, Cv, hn, Ss)

' H7. Limit deposition velocity for pipes, SI units
' Function Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dn_Ss(d50, Cv, dn, Ss)

' H8. Limit deposition velocity for pipes with input of interior dimension, SI units
' Function Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dinterior_Ss(d50, Cv, di, Ss)

' H9. Limit deposition velocity for pipes, Imperial units
' Function Slurry_Limit_Deposition_Velocity_JRI_Imp_d50_Cv_dn_Ss(d50, Cv, dn, Ss)

' H10. Limit deposition velocity for pipes, including lining, Imperial units
' Function Slurry_Limit_Deposition_Velocity_Lining_JRI_Imp_d50_Cv_dn_Ss_Slining(d50, Cv, dn, Ss, Slining)

## 2. Deduction of slurry props.
				#REF!
				Page 1 of 4
Deductioin of equations for slurry properties

				Page 2 of 4
Volume concentration

				Page 3of 4
Pulp density and specific gravity

				Page 4 of 4

## 3a
				#REF!
3a.- Applications of deducted equations (valid for any value of the liquid density)

Slurry data

Cw =	0,3	-		Specific gravity of liqid				Density of pulp		Eq. (u)
rs =	2800	kg/m3		SL =	rL / rw
rL =	1150	kg/m3		rL =	1150	kg/m3
d50 =	16	mm		rw =	1000	kg/m3
t =	10	ºC		SL =	1,15	-		rp =	rL * (1-Cv) / (1 - Cw)
				rL =	1150	kg/m3
Water density at termperature				Volumetric concentration				Cv =	0,1497	-
rw=	SaturatedWaterDensity_t					Eq. (n)		Cw =	0,3
t =	10	ºC					rp =	1397	kg/m3
rw=	1000	kg/m³
				Specific gravity of pulp
Specific gravity of solids		-		Cv =	1/ (1 +((1-Cw)/Cw)*rs/rL )					Eq. (v)
Ss =	rs / rw			Cw =	0,3	-
rs =	2800	kg/m3		rs =	2800	kg/m3
rw =	1000	kg/m3		rL =	1150	kg/m3
Ss =	2,43	-		Cv =	0,150	-		Sp =	SL * (1 - Cv) / ( 1 - Cw)
				SL =	1,15	-				Note
				Cv =	0,1497	-				The equation numbers correspond to sheet 2
				Cw =	0,3	-
				Sp =	1,397

## 3b
Slurry data				3b.- Application of equations from sheet Ref. 4 . Equations valid only if the liquid is water

Cw =	0,3	-
rs =	2800	kg/m3
rL =	rw	kg/m3							rp =	rL * (1+ Cv * (Ss - 1) )
d50 =	16	mm		rp =	rL * Ss / (Cw+(1-Cw)*Ss)			Cv =	(rp - rL) / (rs - rL)			rL =	1000,0	kg/m3		Cw =	Ss * Cv / ( 1 + (Ss - 1)*Cv)
t =	10	ºC		rL =	1000,0	kg/m3		rp =	1238,94	kg/m3		Cv =	0,133	-		Ss =	2,80
				Cw =	0,3	-		rL =	1000,0	kg/m3		Ss =	2,80			Cv =	0,133
Water density at termperature				Ss =	2,80	-		rs =	2800	kg/m3		rp =	1239	kg/m3		Cw =	0,30
rw=	SaturatedWaterDensity_t			rp =	1239	kg/m3		Cv =	0,133	-
t =	10	ºC
rw=	1000	kg/m³		Specific gravity of pulp
rL= rw	1000	kg/m³		Sp =	rp / rw
				rL =	1239	kg/m3		Cv =	(Sp - 1) / ( Ss - 1)			Sp =	Ss / ( Cw + (1 - Cw) * Ss )
Specific gravity of solids				rw =	1000,0	kg/m3		Sp =	1,24	-		Ss =	2,80	-
Ss =	rs / rw			Sp =	1,24	-		Ss =	2,80	-		Cw =	0,3	-
rs =	2800	kg/m3						Cv =	0,133	-		Sp =	1,24
rw =	1000,0	kg/m3
Ss =	2,80	-

Specific gravity of liqid									Sp =	1 + Cv * (Ss - 1 )
SL =	rL / rw			Cw =	(Sp - 1) * Ss / ( (Ss-1)*Sp)			Cv =	Cw / (Ss * (1 - Cw)+ Cw )			Cv =	0,133
rL =	1000,0	kg/m3		Sp =	1,24	-		Cw =	0,3	-		Ss =	2,80
rw =	1000,0	kg/m3		Ss =	2,80	-		Ss =	2,80	-		Sp =	1,24
SL =	1,00	-		Cw =	0,30	-		Cv =	0,133	-

## 3c
				3 of 3
Slurry data				3c.- Equations from Slurry Systems Handbook. From sheet Ref. 1 (valid for any value of the liquid density)

Cw =	0,3	-
rs =	2800	kg/m3
rL =	1150	kg/m3
d50 =	16	mm		rp =	100 / (Cw/rs +(100-Cw)/rL )					Cw =	Cv*rs / rp
t =	10	ºC		Cw =	30	%					Cv =	0,150	-
				rs =	2,8	t/m3		Cv = (Cw/rs)/( Cw/rs)+(100-Cw)/rL)				rs =	2,8	t/m3
Water density at termperature				rL =	1,15	t/m3		Cw =	30	%		rp =	1,40	t/m3
rw=	SaturatedWaterDensity_t			rp =	1,397	t/m3		rs =	2,8	t/m3		Cw =	0,30	-
t =	10	ºC					rL =	1,15	t/m3
rw=	1000	kg/m³					Cv =	0,150	-

Specific gravity of solids		-
Ss =	rs / rw			Cv =	Cw*rp / rs
rs =	2800	kg/m3		Cw =	30	%
rw =	1000	kg/m3		rs =	2,8	t/m3
Ss =	2,80	-		rp =	1,40	t/m3
				Cv =	14,97	%		Cv = (Cw/rs) / ( Cw/rs) + (1-Cw)/rL)
Specific gravity of liqid		-					Cw =	0,3	-
SL =	rL / rw					rs =	2,8	t/m3
rL =	1150	kg/m3					rL =	1,15	t/m3
rw =	1000	kg/m3					Cv =	0,150	-
SL =	1,15	-

## 4 Limit deposition velocity
				#REF!
	Limit deposition velocity "vL" according [1]

		Nominal diameter in inches and schedule standard					Nominal diameter in milimeters and schedule standard					Interior diameter in milimeters

		Application (Imp)					Application (SI)					Application (Imput in milimeters)
		d50 =	250	mm	d50 >= 200 mm					d50 =	250	mm	d50 >= 200 mm					d50 =	250	mm	d50 >= 200 mm
		Cv =	25	%	5% <= Cv <= 40%					Cv =	25	%	5% <= Cv <= 40%					Cv =	25	%	5% <= Cv <= 40%
		dn =	4	in	any diameter					dn =	100	mm	any diameter					d =	102	mm	any diameter
		SS =	4,15	-					SS =	4,15	-					SS =	4,15	-

For particle diameter d50 >= 200mm,		Using the VBA function
This equation is used for any diameter,		VL =	Slurry_Limit_Deposition_Velocity_JRI_Imp_d50_Cv_dn_Ss					VL =	Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dn_Ss					VL =	Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dinterior_Ss
since there is not any equation		VL =	2,79	m/s					VL =	2,79	m/s					VL =	2,79	m/s
proposed for large diameters in [1]
		Using the equation					Velocidad límite de decantación					Limit deposition velocity
		vL =	FL * (2* g * d * (SS -1))^0.5		[Ec.b]					vL =	FL * (2* g * d * (SS -1))^0.5		[Ec.b]					vL =	FL * (2* g * d * (SS -1))^0.5		[Ec.b]
		FL =	1,110	-					FL =	1,110	-					FL =	1,110	-
		g =	9,81	m/s2					g =	9,81	m/s2					g =	9,81	m/s2
		d :	0,10226	m					d :	0,102	m					d :	0,102	m
		SS =	4,15	-					SS =	4,15	-					SS =	4,15	-
		vL =	2,79	m/s					vL =	2,79	m/s					vL =	2,79	m/s

		Application (Imp)					Application (SI)					Application (Imput in milimeters)
		d50 =	150	mm	d50 < 200 mm					d50 =	150	mm	d50 < 200 mm					d50 =	150	mm	d50 < 200 mm
		Cv =	25	%	5% <= Cv <= 40%					Cv =	25	%	5% <= Cv <= 40%					Cv =	25	%	5% <= Cv <= 40%
		dn =	8	in	D > 8 in					dn =	200	mm	D > 200 mm					d =	300	mm	D > 200 mm
		SS =	4,15	-					SS =	4,15	-					SS =	4,15	-

		Using the VBA function					Using the VBA function					Using the VBA function
For particle diameter d50 < 200mm,		VL =	Slurry_Limit_Deposition_Velocity_JRI_Imp_d50_Cv_dn_Ss					VL =	Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_D_Ss					VL =	Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dinterior_Ss
tubes of large diameter d > 150 mm		VL =	2,36	m/s					VL =	2,36	m/s					VL =	2,61	m/s
and for fine-grained solids, narrow					Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dinterior_Ss(d50, Cv, di, Ss)
particle size spectrum.		Using the equation			[Eq. C]					Using the equation			[Eq. C]					Using the equation			[Eq. C]
		vL =	vL =	1.25 *FL * (2* g * d * (SS -1))^0.25					vL =	1,25 * FL * (2* g * d * (SS -1))^0.25					vL =	1,25 * FL * (2* g * d * (SS -1))^0.25
		FL =	1,005	-					FL =	1,005	-					FL =	1,005	-
		g =	9,81	m/s2					g =	9,81	m/s2					g =	9,80665	m/s2
		d :	0,20274	m					d :	0,203	m					d :	0,300	m
		SS =	4,15	-					SS =	4,15	-					SS =	4,15	-
		vL =	2,36	m/s					vL =	2,36	m/s					vL =	2,61	m/s

		Application (Imp)					Application (SI)					Application (Imput in milimeters)
		d50 =	150	mm	d50 < 200 mm					d50 =	150	mm	d50 < 200 mm					d50 =	150	mm	d50 < 200 mm
		Cv =	25	%	5% <= Cv <= 40%					Cv =	25	%	5% <= Cv <= 40%					Cv =	25	%	5% <= Cv <= 40%
		dn =	4	in	D <= 8 in					dn =	100	mm	D <= 200 mm					dn =	102	mm	D <= 200 mm
		SS =	4,15	-					SS =	4,15	-					SS =	4,15	-

		Using the VBA function					Using the VBA function					Using the VBA function
For particle diameter d50 < 200mm,		VL =	Slurry_Limit_Deposition_Velocity_JRI_Imp_d50_Cv_Dn_Ss					VL =	Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dn_Ss					VL =	Slurry_Limit_Deposition_Velocity_JRI_SI_d50_Cv_dinterior_Ss
tubes of small diameter d <= 150 mm		VL =	2,21	m/s					VL =	2,21	m/s					VL =	2,21	m/s
and for fine-grained solids, narrow
particle size spectrum.		Using the equation			[Eq. A]					Using the equation			[Eq. A]					Using the equation			[Eq. A]
		vL =	1.1 *FL * (2* g * d * (SS -1)^0.6)^0.5					vL =	1.1 *FL * (2* g * d * (SS -1)^0.6)^0.5					vL =	1.1 *FL * (2* g * d * (SS -1)^0.6)^0.5
		FL =	1,005	-					FL =	1,005	-					FL =	1,005	-
		g =	9,81	m/s2					g =	9,81	m/s2					g =	9,81	m/s2
		d :	0,10226	m					d :	0,102	m					d :	0,102	m
		SS =	4,15	-					SS =	4,15	-					SS =	4,15	-
		vL =	2,21	m/s					vL =	2,21	m/s					vL =	2,21	m/s

			vL =	1.1 * FL * ( 2 * g * d * (Ss - 1)^0.6 )^0.5					[1] Eq. a

			vL =	FL * ( 2 * g * d * (Ss - 1) )^0.5					[1] Eq. b

			vL =	1.25 * FL * ( 2 * g * d * (Ss - 1) )^0.25					[1] Eq. c

## Cp
Specific heat of a pulp
					Specific heat of pulp

					Cpp =	Cw * Cps + (1-Cw)*Cpwater

					Mas concentration of solid in pulp
CP: specific heat					Cw =	0,3	-
Cw: weiight concentration					Specific heat of solids
					Cps =	0,8	kJ/(kg*K)
Index:					Specific heat of water
p: pulp					Cpwater =	4,184	kJ/(kg*K)
s: solids					Resulting specific heat of pupl
L: liquid					Cpp =	3,17	kJ/(kg*K)

## Ref. 1
Application of equations from Slurry Systems Handbook [1].

					(1-6a)
			(1-4)

					Cw =	Cv*rs / rm
					Cv =	18,67	%
rm =	100 / (Cw/rs +(100-Cw)/rL )				rm =	1,74	t/m3			rs =	(Cw/100) *rm*rL / ( rL - (1 - Cw/100)*rm )
Cw =	30	%			rs =	2,8	t/m3			Cw =	30	%
rs =	2,8	t/m3			Cw =	30	%			rm =	1,74	t/m3
rL =	1,5	t/m3					rL =	1,5	t/m3
rm =	1,74	t/m3					rs =	2,8

			(1-5a)					(1-5b)

Cv =	Cw*rm / rs					Cv =	100/ (1 +((100-Cw)/Cw)*rs/rL )
Cw =	30	%					Cw =	30	%
rs =	2,8	t/m3					rs =	2,8	t/m3
rm =	1,74	t/m3					rL =	1,5	t/m3
Cv =	18,67	%					Cv =	18,67	t/m3

## Ref. 2
Slurry Transport Using Centrifugal pumps [2]

					Slurry Transport Using Centrifugal pumps [2]

## Ref. 4
	JRI Annex B [4]

						Valid only if / liquid is water

[1a] / [2a] / [3a] / [4a] / [1b] / [2b] (f) / [3b] / [4b]

		Limit deposition velocity

		[1], pages 20 and 21

						[1], page 20, equation for case "a"
						vL =	1.1 * FL * ( 2 * g * d * (Ss - 1)^0.6 )^0.5				[1] Eq. a

						[1], page 20, equation for case "b"
						vL =	FL * ( 2 * g * d * (Ss - 1) )^0.5				[1] Eq. b

						[1], page 21, equation for case "c"
						vL =	1.25 * FL * ( 2 * g * d * (Ss - 1) )^0.25				[1] Eq. c

	[1], pages 15 to 22

## Ref. 5
Warman Slurry Pumping Handbook [5]

					Function Slurry_Fl_McElvain_d50_Cv(d50, Cv)

					The function Slurry_Fl_McElvain_d50_Cv gives the Fl deposition velocity correction
					factor fromMc Elvain and Cave, as a function of the particle size d50 [microns]
					and the volume concentration CV [%]

					Range of validity for the average particle size:
					10 microns < d50 < 3000 microns

					Range of validity for the volume concentration:
					5 % < Cv < 40 %

					Application
					FL =	Slurry_Fl_McElvain_d50_Cv(d50, Cv)
					d50 =	400	mm
					Cv =	30	%
					FL =	1,24	-

## Ref. 6
Weir Slurry Pumping Manual [6]

	Cv =	(Sp-1) / (Ss-1)		(valid if rL=rw)
	Sp =	1,239		-
	Ss =	2,8		-
	Cv =	0,133		-

## 1. Manning
				Page 1 of 5

				[3]

The Maning equation relates the velocity of a fluid in an open channel, to properties of the open channel.

It was introduced by the Irish Engineer Robert Manning in 1889 as an alternative to the Chezy Equation.
The Mannings equation is an empirical equation that applies to uniform flow in open channels and is a
function of the channel velocity, flow area and channel slope.

Q: flow rate (m³/s)
Rh: hydraulic radius (m)
Rh = A/P
A: area of fluid section (m²)
P: wetted perimeter (m)
S: slope (-)
N: Manning coefficient
This coefficient is a function of
the channel material

				Page 2 of 5

Darcy-Weisbach equation adapted to match the structure of Manning's equation

				Page 3 of 5

				Page 4 of 5

				Page 5 of 5
Manning's coefficient for a
circular pipe, full, required
in the Manning's equation, to					An equation defining the Manning's coefficient and that makes that the
be equivalent with the Darcy-					Manning's equation is equivalent to the Darcy-Weisbach equation
Weisbach equation

				N: Manning's coefficient

				ND: Manning's coefficient required to make
				that the Manning's equations is equivalent
				to the Darcy-Weisbach equation

				Thus, when using the Manning's equation with
				a Manning's coefficient defined with Eq. (11),
				the obtained result wil be the same as the one
				obtained when using the Darcy-Weisbach
				equation.
				For a circular pipe, full

## 1a. Manning apps
				Page 1 of 2
Flow rate according Manning, using a calculated Manning coefficient					Reynolds number				Slope				Flow rate according Mannings
				Re =	v * d / n			S =	DH / L
Fluid:	water			Liquid properties				v =	3,37	m/s		DH =	10,00	m
t =	10	ºC		t =	10	ºC		d =	0,3	m		L =	300
Pipe					n =	1,30E-06	m²/s		S =	0,0333
d =	300	mm		Dynamic viscosity				Re =	7,8E+05	-
Rabs =	0,15	mm		m = SaturatedWaterAbsoluteViscosity_t					Circular pipe, full				Qcalc =	(A / N) * Rh^(2/3) * S^(1/2)
L =	300	m		m =	0,0013	Pa s		Friction factor					A =	0,0707	m³
Elevation difference				Density				RabsMM =	0,15	mm					N =	0,0096	-
DH =	10	m		r = SaturatedWaterDensity_t				dMM =	300	mm					Rh =	0,0750	m
				r =	1000	kg/m³		Rrel =	0,0005	-					S =	0,0333	-
d =	0,3	m		Kinematic viscosity				Re =	777.906	-		Mannings' coefficient				Qcalc =	0,2379	m³/s
Rabs =	0,00015	m		n =	m / r			f =	0,017316607704803			N = ( f * d^(1/3) / (2^(11/3) * g) )^0.5				Qcalc =	856,404	m³ /h
				m =	0,0013	Pa s					f =	0,01732
Flow rate initially assumed				r =	1000	kg/m³		Kinematic pressure				d	0,3			DQ =	Qass - Qcalc
Qass =	856,40	m³/h		n =	1,30E-06	m²/s		Pk =	v^2 /( (2*g)			N =	0,00965			Qass =	856,40	m³ /h
Qass =	0,24	m³/s					v =	3,37	m/s					Qcalc =	856,40	m³ /h
				Flow velocity				Pk =	0,58	m					DQ =	0,000	m³ /h
Pipe section area				v =	Q / A					Iteration finished
A =	(p/4) * d^2			Q=	0,24	m³/s		Hydraulic radius					(Using Goal seek)
d =	0,3	m		A =	0,0707	m²		Rh =	d/4
A =	0,0707	m²		v =	3,37	m/s		d =	0,3	m
				Rh =	0,075	m

g =	9,80665	m/s²					From [3], the Manning coefficient for a new unlined steel is 0.0110
				That is, a value		15,5	% greater than the calculated value

				Page 2 of 2
From [3], the Manning coefficient for a new unlined steel is 0.001

[3]

## 2. Hazen Williams
				Page 1 of 4
Hazen Williams equation
				[3]

	R =	A / P
	A: area of fluid section (m²)
	P: wetted perimeter (m)

Hazen Williams empirical equation for friction head loss

The Hazen Williams equation was developed for water at
temperatures normally experienced in potable water
systems, for pipe diameters d >= 50 mm and within a
moderate range of water velocity v <= 3 m/s.

				Page 2 of 4

				Page 3 of 4

				http://www.engineeringtoolbox.com/william-hazens-equation-d_645.html

				In the equation of the reference, the diameter indicated is not
				the hydraulic diameter. It is the interior pipe diameter.

				Page 4 of 4

## 3. Darcy-Weisbach
				Page 1 of 6

Darcy-Weisbach equation for pressure loss

				Page 2 of 6

				Page 3 of 6

				Page 4 of 6

				Page 5 of 6

				Page 6 of 6
From sheet 1. Manning equation

## 4. Channels
				Page 1 of 1
Velocity in channels according Manning and Darcy-Weisbach equations

				From sheet 1

				Thus, if the velocity is calculated with the
				Manning's equation (13) and the Manning
				coefficient is evaluated using equation (11),
				the result will be identical as the one
				obtained using the Darcy equation (12).

				See also [1]

## 5. Friction factors
https://en.wikipedia.org/wiki/Darcy_friction_factor_formulae#Swamee.E2.80.93Jain_equation

f =	Pipe_Friction_Factor_Rrel_Re					Swamee
RabsMM =	0,1	mm					RabsMM =	0,1	mm
dMM =	300	mm					dMM =	300	mm
Rrel =	Rabs / d					Re =	100.000	-
Rrel =	0,000333333333333
Re =	100.000	-					A =	-2*LOG( Rabs/(3.7*d) + 12/Re )
f =	0,01960					fswamee =	0.25 * ( Log10( Rabs/(3.7*d) + 5.74 / Re^0.9 ) )^-2					A =	7,35518886539936

					Rabs =	0,1	mm					B =	-2*LOG( Rabs/(3.7*d) + 2.51*A/Re )
Turbulent flow					d =	300	mm					B =	7,12226582616982
					Re =	100.000	-
					fswamee =	0,01966					C =	-2*LOG( Rabs/(3.7*d) + 2.51*B/Re )
					C =	7,14095096375765

					1/f^(0.5) =	A -(B-A )^2 / ( C-2*B+A )
					1/f^(0.5) =	7,13956335238869
					1/f =	50,9733648627716
					f =	0,01962
Laminar flow

Churchill equation for Darcy friction factor f, for laminar and turbulent flow
Spans all fluid-flow regimes

Rrel =	0,0003
Re =	100.000

A =	( - 2.457 *Ln( ( (7/Re )^0.9 + 0.27*Rrel )^-1 ) )^16
A =	7,49984222167614E+020

B =	( 37530 / Re )^16
B =	1,54902001950605E-07

f =	8 * ( (8/Re)^12 + (A + B)^(-1.5 ) )^(1/12)
f =	0,01967

[7]

Laminar zone
Re <= 2000
Equation 2

Critical zone
2000 < Re < 4000
Flow is unstable and can exhibit either laminar or turbulent behavior

Transition and turbulent zone
Re >= 4000
Equation 3

## 6. Colebrook
Colebrook-White equation using decimal logarithmus

					Page 1 of 3

					Decimal logarithmus

					Darcy

					Fanning

					Page 2 of 3
	Colebrook-White equation using natural logarithmus					Natural logarithmus

					Darcy

					Fanning

					Page 3 of 3
	Colebrook equation		[10], page 218				Colebrook in decimal logarithmus, Darcy-Weisbach friction factor

					For circular full pipes

					For a general shape

## Ref_0
[1]

[2]

[3]

[4]	Curso de transporte hidraulico de solidos
	Tecnex
	JRI

[5]

					Carlos J. Cruz
					www.piping-tools.net
					cjcruz15@vtr.net

[6]	Slurry pumping manual
	Warman International Ltd.
	1st edition, 2002

[21]	http://www.azom.com/article.aspx?ArticleID=1417				Ex [3]

[22]	http://taninos.tripod.com/mallas.htm				Ex [4]

## Ref
[1]
	http://www.fsl.orst.edu/geowater/FX3/help/8_Hydraulic_Reference/Darcy_Friction_Factor.htm

[2]	Fluid flow in pipes
	CIVE2400 Fluid Mechanics

	http://www.efm.leeds.ac.uk/CIVE/CIVE2400/pipe_flow2.pdf

[3]

[4]

	http://www3.ntu.edu.sg/home/cnscheng/Publications/reprint/Note%20Nikuradse%20transition%20interpolation.pdf

[5]

	http://www.members.optusnet.com.au/msephton/wip/rel_darcy_manning.pdf

[6]	PDF]Survey in Colebrook equation approximations Abstract: Introduction:

	gpcpublishing.com/index.php?journal=gjm&page=article&op...57...pdf...
	Apr 17, 2015 - study involved free surface flow. Keywords: Colebrook, equation, friction factor. Introduction: Compact forms: The Colebrook equation is an ...

	https://www.google.cl/url?sa=t&rct=j&q=&esrc=s&source=web&cd=6&cad=rja&uact=8&ved=0ahUKEwjs17y3nvbNAhUJhpAKHTzxC0kQFggyMAU&url=http%3A%2F%2Fgpcpublishing.com%2Findex.php%3Fjournal%3Dgjm%26page%3Darticle%26op%3Ddownload%26path%255B%255D%3D57%26path%255B%25

[7]

[8]	Applicability of the Colebrook-White Formula to Represent Frictional Losses in
	Partially Filled Unsteady Pipeflow

	http://nvlpubs.nist.gov/nistpubs/jres/088/jresv88n6p389_A1b.pdf

## Ref1
[1]	http://www.fsl.orst.edu/geowater/FX3/help/8_Hydraulic_Reference/Darcy_Friction_Factor.htm

						N =	( f * Rh^(1/3) / ( 8 * g ))^0.5

						N =	Rh^(1/6) * ( f / (8*g ) )^0.5

## Ref2
	http://www.efm.leeds.ac.uk/CIVE/CIVE2400/pipe_flow2.pdf

[2]

## Ref3
[3]

	ks = Rabs : effective roughness od absolure rugosity
	R = Rh : Hydraulic radius Rh = A / P

## Ref4
Friction factor for open channel flow				[4]	Page 11

## Ref7
[7]		http://www.jmcampbell.com/tip-of-the-month/2007/02/friction-pressure-drop-calculation/

							Laminar zone
							Re <= 2000
							Equation 2

							Critical zone
							2000 < Re < 4000
							Flow is unstable and can exhibit either laminar or turbulent behavior

							Transition and turbulent zone
							Re >= 4000
							Equation 3

## Ref8
[8]

The complete reference
Journal of research of the National Bureau of standards. Vol 88, No 6, November-December 1983
is to be found in
www.piping-tools.net.
Pipes. Flow rate and pressure loss equations.xlsm