## Chart
				Rev. cjc.28.06.2017
Psychrometric chart for a height above sea level					Process line shown with a blue thick line
H =	0	m.a.s.l.			(see sheet Process)

				Sicro_Absolute_Humidity_tdb_f_H

tdb	Relative humidity f = Sicro_Absolute_Humidity_tdb_f_H [%]
	f = 10%	f = 20%	f = 30%	f = 40%	f = 50%	f = 60%	f = 70%	f = 80%	f = 90%	f = 100%
ºC	10	20	30	40	50	60	70	80	90	100
0	0,0004	0,0008	0,0011	0,0015	0,0019	0,0023	0,0026	0,0030	0,0034	0,0038
5	0,0005	0,0011	0,0016	0,0021	0,0027	0,0032	0,0038	0,0043	0,0049	0,0054
10	0,0008	0,0015	0,0023	0,0030	0,0038	0,0046	0,0053	0,0061	0,0069	0,0076
15	0,0010	0,0021	0,0032	0,0042	0,0053	0,0063	0,0074	0,0085	0,0096	0,0106
20	0,0014	0,0029	0,0043	0,0058	0,0073	0,0087	0,0102	0,0117	0,0132	0,0147
25	0,0020	0,0039	0,0059	0,0079	0,0099	0,0119	0,0139	0,0160	0,0180	0,0201
30	0,0026	0,0053	0,0079	0,0106	0,0133	0,0160	0,0188	0,0216	0,0244	0,0272
35	0,0035	0,0070	0,0105	0,0141	0,0178	0,0214	0,0252	0,0289	0,0327	0,0366
40	0,0046	0,0092	0,0139	0,0187	0,0235	0,0284	0,0334	0,0385	0,0437	0,0489
45	0,0059	0,0120	0,0182	0,0245	0,0309	0,0375	0,0441	0,0510	0,0579	0,0650
50	0,0077	0,0155	0,0236	0,0319	0,0404	0,0491	0,0580	0,0672	0,0766	0,0863
55	0,0098	0,0200	0,0304	0,0413	0,0524	0,0640
60	0,0125	0,0255	0,0390	0,0532
65	0,0158	0,0323	0,0498
70	0,0198	0,0408	0,0633
75	0,0246	0,0513
80	0,0305
85	0,0377
90	0,0463
95	0,0567
100

tdb	Enthalpy h = Sicro_Absolute_Humidity_tdb_ent [kJ/kg]
		h = 10	h = 20	h = 30	h = 40	h = 50	h = 60	h = 70	h = 80	h = 90	h = 100	h = 110	h= 120
ºC	0	10	20	30	40	50	60	70	80	90	100	110	120
0	0,0000	0,0040	0,0080	0,0120
5		0,0020	0,0060	0,0100	0,0139
10		0,0000	0,0040	0,0079	0,0119	0,0159	0,0198	0,0238	0,0278	0,0318	0,0357	0,0397	0,0437
15			0,0020	0,0059	0,0099	0,0138	0,0178	0,0218	0,0257	0,0297	0,0336	0,0376	0,0415
20			0,0000	0,0039	0,0079	0,0118	0,0158	0,0197	0,0236	0,0276	0,0315	0,0355	0,0394
25				0,0020	0,0059	0,0098	0,0137	0,0177	0,0216	0,0255	0,0295	0,0334	0,0373
30				0,0000	0,0039	0,0078	0,0117	0,0157	0,0196	0,0235	0,0274	0,0313	0,0352
35					0,0019	0,0058	0,0097	0,0136	0,0175	0,0214	0,0253	0,0292	0,0331
40					0,0000	0,0039	0,0078	0,0117	0,0155	0,0194	0,0233	0,0272	0,0311
45					0,0019	0,0058	0,0097	0,0136	0,0174	0,0213	0,0252	0,0290
50					0,0000	0,0039	0,0077	0,0116	0,0154	0,0193	0,0232	0,0270
55					0,0019	0,0058	0,0096	0,0135	0,0173	0,0212	0,0250
60					0,0000	0,0038	0,0077	0,0115	0,0153	0,0192	0,0230
65					0,0019	0,0057	0,0095	0,0134	0,0172	0,0210
70					0,0000	0,0038	0,0076	0,0114	0,0152	0,0190
75					0,0019	0,0057	0,0095	0,0133	0,0171
80					0,0000	0,0038	0,0076	0,0113	0,0151
85					0,0019	0,0057	0,0094	0,0132
90					0,0000	0,0038	0,0075	0,0113
95					0,0019	0,0056	0,0094
100					0,0000	0,0037	0,0075
110					0,0000	0,0037
120					0,0000

tdb	Wet bulb temperature twb = Sicro_Absolute_Humidity_tdb_twb_H [ºC]
	twb = 0	twb = 5	twb = 10	twb = 15	twb = 20	twb = 25	twb = 30	twb = 35	twb = 40
ºC	0	5	10	15	20	25	30	35	40
0	0,0038
5	0,0018	0,0054
10		0,0034	0,0076
15		0,0014	0,0056	0,0106
20			0,0036	0,0086	0,0147
25			0,0016	0,0065	0,0126	0,0201
30				0,0045	0,0105	0,0180	0,0272
35				0,0025	0,0085	0,0159	0,0251	0,0366
40				0,0005	0,0064	0,0138	0,0229	0,0344	0,0489
45					0,0044	0,0117	0,0208	0,0322	0,0466
50					0,0024	0,0097	0,0187	0,0300	0,0444
55					0,0004	0,0076	0,0166	0,0279	0,0422
60					0,0056	0,0145	0,0258	0,0400
65					0,0036	0,0125	0,0236	0,0378
70					0,0016	0,0104	0,0215	0,0356
75					0,0084	0,0195	0,0335
80					0,0064	0,0174	0,0313
85					0,0044	0,0153	0,0292
90					0,0024	0,0133	0,0271
95					0,0004	0,0113	0,0250
100					0,0092	0,0229
Psychrometric chart
Dry bulb temperature ºC
Absolute humidity kg-w/kg-da
Relative humidities %
Enthalpies kJ/kg
Wet bulb temperatures ºC

## Table
				Rev. cjc.28.06.2017
Psychrometric Functions

	Dry bulb temperature		tdb	°C		Absolute humidity		x	kg w/kg da		Dew point temperature		tdp	ºC
	Relative humidity		f	%		Specific volume		v	m3/kg da		Specific enthalpy		ent	kJ/kg da
	Height above sea level		H	m.a.s.l.		Density		r	kg /m3		Wet bulb temperature		twb	ºC

	In the functions to calculate the wet bulb temperature (functions 16, 36, 46 and 56), some limits to the input values of the dry bulb					Maximum values for the input parameters
	temperature, relative humidity and height above sea level have been set to to obtain an acceptable maximum number of iterations.					tdbMax =	96	°C
				f Max =	60	%
	The numbers in square brackets indicate the number of the function in the Basic environment					Hmax =	5300	m.a.s.l.

		Groups
			Group 1			Group 2			Group 3			Group 4			Group 5
			tdb, f , H			tdb, twb, H			tdb, x, H			ent, x, H			tdb, ent, H
tdb	ºC	tdb	21,0	°C	tdb	21,0	°C	tdb	21,0	°C	tdb	21,0	[48]	tdb	21,0	°C
f	%	f	31,5	%	f	31,5	[27]	f	31,5	[37]	f	31,5	[47]	f	31,5	[57]
H	m s.n.m.	H	10,0	m	H	10,0	m	H	10,0	m	H	10,0	m	H	10,0	m
x	kg/kg	x	0,00485	[11]	x	0,0048	[21]	x	0,0048	kg/kg	x	0,0048	kg/kg	x	0,0048	[51]
v	m3/kg	v	0,841	[12]	v	0,841	[22]	v	0,841	[32]	v	0,841	[42]	v	0,841	[52]
r	kg/m3	r	1,195	[13]	r	1,195	[23]	r	1,195	[33]	r	1,195	[43]	r	1,195	[53]		www.piping-tools.net
tdp	ºC	tdp	3,44	[14]	tdp	3,44	[24]	tdp	3,44	[34]	tdp	3,44	[44]	tdp	3,44	[54]		Psychrometric functions_Deductions.xls
ent	kJ/kg	ent	33,3	[15]	ent	33,3	[25]	ent	33,30	[35]	ent	33,30	kJ/kg	ent	33,30	KJ/kg		Rev. cjc. 30.03.2016
twb	ºC	twb	11,77	[16]	twb	11,77	ºC	twb	11,77	[36]	twb	11,77	[46]	twb	11,77	[56]		cjcruz[at]piping-tools-net

## Process
Nat-Nat diagram
Process is a straight line between points 1 and 2.
					x =	x1 + (t - t1 ) * (x2 - x1) / (t2 - t1)
Specification for point 1
Temperature	t1 =	55	ºC			t1 =	55	ºC
Relative humidity	f1 =	50	%			t2 =	25	ºC
	H =	0	m.a.s.l.			x1 =	0,0524	kg/kg
					x2 =	0,0059	kg/kg
	x1 =	0,0524	kg/kg
					t	x
Specification for point 2					ºC	kg/kg
Temperature	t2 =	25	ºC			25	0,0059
Relative humidity	f2 =	30	%			26	0,0074
	H =	0	m.a.s.l.			27	0,0090
					28	0,0105
	x2 =	0,0059	kg/kg			29	0,0121
					30	0,0137
					31	0,0152
					32	0,0168
					33	0,0183
					34	0,0199
					35	0,0214
					36	0,0230
					38	0,0261
					40	0,0292
					42	0,0323
					44	0,0354
					46	0,0385
					48	0,0416
					50	0,0447
					52	0,0478
					54	0,0509
					55	0,0524

In the psychrometric chart for height above sea level H = 0 m.a.s.l
I have included the proces 1 - 2 wich consist of linear function
x = function (t)
The equation for this function is shown in sheet Process.

For adding the information of aprocess line in a psychrometric chart, see sheet "H = 0 m.a.s.l"

## Ref
[1]	Ashrae Handbook
	2005 Fundamentals

[2]	Ashrae Handbook
	1985 Fundamentals

[3]	A quick derivation relating altitude to air pressure
	Version 1.03, 12/22/2004
	2004 Portland State Aerospace Society <http://www.psas.pdx.edu>
	Redistribution allowed under the terms of the GNU General Public License version 2 or later.

	http://psas.pdx.edu/RocketScience/PressureAltitude_Derived.pdf

	www.piping-tools.net
	Psychrometric functions_Deductions.xls
	Rev. cjc. 30.03.2016
	cjcruz[at]piping-tools-net