## Steam Properties
Magnus Holmgren [1]

Saturation properties	p =	1	bar	Steamdat	Added		Humid region					Added		Superheated steam	p =	1	bar
		Magnus		(for p = 1 bar)	functions				Magnus		Steamdat	functions			t =	100	ºC	Steamdat	Added
SaturSteam_Entropy_p(p)	sV_p =	7,36	kJ(kg K)	7,36				p =	10	bar	(for p = 1 bar, x = 0.8)					Magnus		(for p = 1 bar, t = 100 ºC)	functions
SaturWater_Entropy_p(p)	sL_p =	1,3	kJ(kg K)	1,3				x =	0,8	-				H2O_Entropy_t_p(t,p)	s_pT =	7,36	kJ/(kg K)	7,36
H2O_SaturationTemp_p(p)	Tsat_p =	99,61	ºC	99,6				Tsat_p =	179,89	ºC	179,89			H2O_Enthalpy_t_p(t,p)	h_pT =	2675,77	kJ/kg	2675,8
SaturWater_Enthalpy_t(t)	hL_p =	417,44	kJ/kg	417,4					H2O_SpecVolume_p_h(t,p)	v_pT =	1,7	m3/kg	1,7
					H2O_Enthalpy_p_x(p,x)	h_px =	2374,2	kJ/kg	2374,2
Saturated water					H2O_Enthalpy_t_x(t,x)	h_Tx =	2374,2	kJ/kg	2374,2			H2O_DynViscosity_t_p(t,p)	my_pT =	1,23E-05	Pa s	1,23E-05
H2O_SaturationPressure_s(s)	-		bar	1			H2O_Entropy_p_h(p,h)	s_pH =	5,7	kJ/(kg K)	5,7				my_ph =	1,23E-05	Pa s
H2O_SaturationPressure_t(t)	psat_T =	1	bar	1			H2O_SpecVolume_p_x(p,x)	v_px =	0,16	m³/kg	0,1557	7.16			my_ps =	1,23E-05	Pa s
H2O_SaturationTemp_s(s)	-		ºC	99,6			H2O_SpecVolume_t_x(t,x)	v_tx =	0,16	m³/kg	0,1557	7,17		H2O_KinemViscosity_t_p(t,p)	ny_pT =	2,08E-05	m²/s		7,1
SaturWater_DynViscosity_t(t)	-		Pa s	2,80E-04			SteamQuality_p_h(p,h)	x_ph =	0,8	-	0,8				ny_ph =	2,08E-05	m²/s		7,2
SaturWater_Enthalpy_p(p)	hL_p =	417,44	kJ/kg	417			SteamQuality_p_s(p,s)	x_ps =	0,8	-	0,8				ny_ps =	2,08E-05	m²/s		7,3
SaturWater_Enthalpy_t(t)	hL_t =	417,44	kJ/kg	417			SteamQuality_t_s(t,s)	x_ts =	0,8	-	0,8	7.20		H2O_Enthalpy_p_s(p,s)	h_ps =	2675,8	kJ/kg	2675,8
SaturWater_Entropy_p(p)	sL_P =	1,3	kJ(kg K)	1,3			H2O_VapourisationHeat_p(p)	hfg_p =	2014,44	kJ/kg	2014,4	7.18		H2O_Enthalpy_t_p(t,p)	h_pt =	2675,8	kJ/kg	2675,8
SaturWater_Entropy_t(t)	sL_t =	1,3	kJ(kg K)	1,3			H2O_VapourisationHeat_t(t)	hfg_t =	2014,44	kJ/kg	2014,4	7.19		H2O_Enthalpy_t_s(t,s)			kJ/kg	2675,8
SaturWater_HeatConduct_t(t)	tcL_t =	0,68	W/(m K)	0,68					h_prho =	2675,8	kJ/kg
SaturWater_Prandtl_p(p)	PrL_P =	1,76	-	1,76	7.12					H2O_Entropy_p_h(p,h)	s_ph =	7,36	kJ/(kg K)	7,36
SaturWater_Prandtl_t(t)	PrL_t =	1,76	-		7.13					H2O_Entropy_t_p(t,p)	s_pt =	7,36	kJ/(kg K)	7,36
SaturWater_SonicVelocity_t(t)	wL_t =	1545,45	m/s	1545,5					H2O_HeatConductivity_t_p(t,p)	tc_pt =	0,0248	W/(m K)	0,0251
	wL_p =	1545,45	m/s					tc_ph =	0,0248	W/(m K)
SaturWater_SpecHeat_Cp_t(t)	CpL_p =	4,22	kJ/(kg K)	4,22					tc_hs =	0,0248	W/(m K)
	CpL_t =	4,22	kJ/(kg K)					H2O_Kappa_p_h(p,h)			-	1,32
SaturWater_SpecVolume_t(t)	vL_T =	0,00104	m³/kg	0,00104					H2O_KappaUp_p_h(p,h)			-	1,32
	vL_p =	0,00104	m³/kg					H2O_KappaDown_p_h(p,h)			-	1,32
SaturWater_Temperature_h(h)	-		ºC	99,6				P =	10	bar				H2O_Prandtl_t_p(t,p)	Pr_pT =	1,027	-	1,015
Water_SurfaceTension_t(t)	st_T =	0,059	N/m	0,059				x =	0,8					Pr_ph =	1,027
	st_p =	0,06	N/m					Tsat =	179,89					H2O_Pressure_t_s(t,s)			bar	1
	rhoL_T	958,64	kg/m³					vg =	0,1943	m³/kg				H2O_Pressure_t_v(t,v)			bar	1
	rhoL_p	958,64	kg/m³					vf =	0,0011	m³/kg					p_hs	1	bar
	uL_T =	417,33	kJ/kg					p_hrho	1	bar
	uL_p =	417,33	kJ/kg					v =	vf + x*(vg – vf)					H2O_SonicVelocity_p_h(p,h)	w_ph =	472,3	m/s	472,3
SaturWater_DynViscosity_p(p)	myL_P =	2,83E-04	Pa s		7.4			vf =	0,0011	m³/kg				H2O_SonicVelocity_t_p(t,p)	w_pT =	472,3	m/s	472,3
SaturWater_DynViscosity_t(t)	myL_t =	2,83E-04	Pa s		7.5			x =	0,8	-					w_ps =	472,3
SaturWater_KinemViscosity_t(t)	nyL_P =	2,95E-07	m²/s		7.8			vg =	0,1943	m³/kg				H2O_SpecificHeat_Cp_t_p(t,p)	Cp_pT =	2,07	kJ/(kg K)	2,07
SaturWater_KinemViscosity_p(p)	nyL_t =	2,95E-07	m²/s		7.9			v =	0,1557	m³/kg					Cp_ph =	2,07	kJ/(kg K)
					Cp_ps =	2,07	kJ/(kg K)
					H2O_SpecificHeat_Cv_t_p(t,p)	Cv_pT =	1,551	kJ/(kg K)	1,551
					Cv_ph =	1,55	kJ/(kg K)
					Cv_ps =	1,55	kJ/(kg K)
					H2O_SpecVolume_p_h(t,p)	v_pT =	1,696	kJ/(kg K)	1,696
					H2O_SpecVolume_p_h(p,h)	v_ph =	1,696	kJ/(kg K)	1,696
Saturated steam					v_ps =	1,696	kJ/(kg K)
SaturSteam_DynViscosity_t(t)	-	-	Pa s	1,20E-05
SaturSteam_Enthalpy_p(p)	hV_p =	2675	kJ/kg	2675					H2O_Temperature_p_h(p,h)	T_ph =	100	ºC	100
SaturSteam_Enthalpy_t(t)	hV_T =	2675	kJ/kg	2675					H2O_Temperature_p_s(p,s)	T_ps =	100	ºC	100
SaturSteam_Entropy_p(p)	sV_p =	7,36	kJ/(kg K)	7,36					H2O_Temperature_p_v(p,v)			ºC	100
SaturSteam_Entropy_t(t)	sV_t =	7,36	kJ/(kg K)	7,36					T_hs =	100	ºC
SaturSteam_HeatConduct_t(t)	tcV_t =	0,025	W/(m K)	0,025					rho_pT =	0,59	kg/m³
SaturSteam_Prandtl_p(p)	PrV_p =	1,03	-	1,02	7,14					rho_ph =	0,59	kg/m³
SaturSteam_Prandtl_t(t)	PrV_t =	1,02			7,15					rho_ps =	0,59	kg/m³
SaturSteam_SonicVelocity_t(t)	wV_T =	472	m/s	472					u_pT =	2506,17	kJ/kg
	wV_p =	472	m/s					u_ph =	2506,18	kJ/kg
SaturSteam_SpecHeat_Cp_t(t)	CpV_T =	2,08	kJ/(kg K)	2,08					u_ps =	2506,18	kJ/kg
	CpV_p =	2,08	kJ/(kg K)
SaturSteam_SpecVolume_t(t)	vV_T =	1,69	m3/kg	1,69
	vV_T =	1,69	m3/kg
SaturSteam_Density	rhoV_T =	0,59	kg/m³
	rhoV_p =	0,59	kg/m³
SaturSpecificEnergy	uV_p =	2505,55	kJ/kg
	uV_T =	2505,55	kJ/kg
SaturVapor_DynViscosity_p(p)	myV_P =	1,23E-05	Pa s		7.6
SaturVapor_DynViscosity_t(t)	myV_t =	1,23E-05	Pa s		7.7
SaturVapor_KinemViscosity_t(t)	nyV_P =	2,08E-05	m²/s		7.1
SaturVapor_KinemViscosity_p(p)	nyVt =	2,08E-05	m²/s		7.11

Approximated value of saturated viscosity
	P =	1	bar
Saturation liquid viscosity(p)	mySatL_p =	2,83E-04	Pa s
Saturation Vapor viscosity(p)	mySatV_p =	1,23E-05	Pa s

These viscosity values allow the Prandtl number to be estimated					Steamdat
					for P = 1 bar
PrSatL_P =	1000* CPL_P(p) * MY_PT(p,(TSAT_P(p)-0.01)) / TCL_T( TSAT_P(p))
PrSatL_P =	1,761					1,760

PrSatV_P =	1000*CPV_P(p) * MY_PT(p,(TSAT_P(p)+0.01)) / TCV_T(TSAT_P(p))
PrSatV_P =	1,028	-					1,015

## Ref
OpenOffice, IF-97 Steam tables.					OpenOffice, IF-97 Steam tables. By: Magnus Holmgren
By: Magnus Holmgren

## Added functions
'___________________________________________________________________________________________________________
'
' 7. Added functions (approximated values are used in some cases) Rev. cjc 27.03.2117
'____________________________________________________________________________________________________________

'7.1.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and t					P =	1	bar
					T =	100	ºC		'7.1.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and t
Function ny_pt(p, t)
					H2O_DynViscosity_t_p(t,p)		my_p,T =	1,23E-05	Pa s		Function ny_pt(p, t)
ny_pt = my_pT(p, t) / rho_pT(p, t)
					RHO_PT		rho_pT =	0,59	kg/m³		ny_pt = my_pT(p, t) / rho_pT(p, t)
End Function
					H2O_KinemViscosity_t_p(t,p)		ny_pT =	my_p,T / rho_pT			End Function
					ny_pT =	2,08E-05	m²/s
					Function:		ny_pT =	2,08E-05	m²/s

'7.2.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and h					P =	1	bar		'7.2.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and h
					T =	100	ºC
Function ny_ph(p, h)					Function ny_ph(p, h)
					H2O_Enthalpy_t_p(t,p)		h_p,T =	2675,77	kJ/kg
ny_ph = my_ph(p, h) / rho_ph(p, h)					ny_ph = my_ph(p, h) / rho_ph(p, h)
					P =	1	bar
End Function					h =	2675,77	kJ/kg		End Function

					my_ph =	1,23E-05	Pa s
					rho_ph =	0,59

					ny_ph =	my_ph / rho_ph
					ny_ph =	2,08E-05	m²/s
					Function:		ny_ph =	2,08E-05	m²/s

'7.3.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and s					P =	1	bar		'7.3.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and s
					T =	100	ºC
Function ny_ps(p, s)					Function ny_ps(p, s)
					H2O_Entropy_t_p(t,p)		s_pT =	7,36	kJ/(kg K)
ny_ps = my_ps(p, s) / rho_ps(p, s)					ny_ps = my_ps(p, s) / rho_ps(p, s)
					P =	1	bar
End Function					s =	7,36	kJ/kg		End Function

					my_ps =	1,23E-05	Pa s
					rho_ps =	0,59
					ny_ps =	my_ps / rho_ps
					ny_ps =	2,08E-05	m²/s
					Function:		ny_ps =	2,08E-05	m²/s

'7.4.- Dynamic viscosity of saturated liquid as function of the pressure					P =	1	bar
					'7.4.- Dynamic viscosity of saturated liquid as function of the pressure
Function myL_P(p)					Tsat_p(p) =	99,61
					Tsat_p(p) -0,1 =	99,51			Function myL_P(p)
myL_P = my_pT(p, (Tsat_p(p) - 0.1))
					myL_P =	my_pT(p; (Tsat_p(p) - 0.1))			myL_P = my_pT(p, (Tsat_p(p) - 0.1))
End Function					myL_P =	2,83E-04	Pa s
					End Functio
					Function:		myL_P(p) =	myL_P(p)
					myL_P(p) =	2,83E-04

'7.5.- Dynamic viscosity of saturated liquid as function of the temperature					T =	99,61	ºC
					'7.5.- Dynamic viscosity of saturated liquid as function of the temperature
Function myL_t(t)
					Function myL_t(t)
myL_t = my_pT((psat_T(t) + 0.1), t)
					myL_t = my_pT((psat_T(t) + 0.1), t)
End Function					myL_t(t)	myL_t(t)
					Function:		myL_t(t)	2,83E-04	Pa s		End Function

'7.6.- Dynamic viscosity of saturated vapor as function of the pressure					P =	1	bar
Function myV_P(p)					'7.6.- Dynamic viscosity of saturated vapor as function of the pressure
					Function myV_P(p)
myV_P = my_pT(p, (Tsat_p(p) + 0.1))
					myV_P = my_pT(p, (Tsat_p(p) + 0.1))
End Function					myV_P(p)	myV_P(p)
					Function:		myV_P(p)	1,23E-05	Pa s		End Function

'7.7.- Dynamic viscosity of saturated vapor as function of the temperature					T =	99,61	ºC
					'7.7.- Dynamic viscosity of saturated vapor as function of the temperature
Function myV_t(t)
					Function myV_t(t)
myV_t = my_pT((psat_T(t) - 0.1), t)
					myV_t = my_pT((psat_T(t) - 0.1), t)
End Function					myV_t(t)	myV_t(t)
					myV_t(t)	1,23E-05	Pa s		End Function

'7.8.- Kinematic viscosity of saturated liquid as function of the pressure					P =	1	bar
					'7.8.- Kinematic viscosity of saturated liquid as function of the pressure
Function nyL_P(p)
					Function nyL_P(p)
nyL_P = my_pT(p, (Tsat_p(p) - 0.1)) / rhoL_p(p)
					nyL_P = my_pT(p, (Tsat_p(p) - 0.1)) / rhoL_p(p)
End Function					nyL_P(p)	nyL_P(p)
					nyL_P(p)	2,95E-07	m²/s		End Function

'7.9.- Kinematic viscosity of saturated liquid as function of the temperature					T =	99,61	ºC
Function nyL_t(t)					'7.9.- Kinematic viscosity of saturated liquid as function of the temperature
					Function nyL_t(t)
nyL_t = myL_t(t) / rhoL_T(t)
					nyL_t = myL_t(t) / rhoL_T(t)
End Function					nyL_t(t)	nyL_t(t)
					nyL_t(t)	2,95E-07	m²/s		End Function

'7.10.- Kinematic viscosity of saturated vapor as function of the pressure					P =	1	bar
					'7.10.- Kinematic viscosity of saturated vapor as function of the pressure
Function nyV_P(p)
					Function nyV_P(p)
nyV_P = my_pT(p, (Tsat_p(p) + 0.1)) / rhoV_p(p)
					nyV_P = my_pT(p, (Tsat_p(p) + 0.1)) / rhoV_p(p)
End Function					nyV_P(p)	nyV_P(p)
					nyV_P(p)	2,08E-05	m²/s		End Function

'7.11.- Kinematic viscosity of saturated vapor as function of the temperature					T =	99,61	ºC
Function nyV_t(t)					'7.11.- Kinematic viscosity of saturated vapor as function of the temperature

nyV_t = my_pT((psat_T(t) - 0.1), t) / rhoV_p(psat_T(t) )					Function nyV_t(t)

End Function					nyV_t = my_pT((psat_T(t) - 0.1), t) / rhoV_p(psat_T(t) )
					nyV_t(t)	nyV_t(t)
					nyV_t(t)	2,08E-05	m²/s		End Function

'7.12.- Prandtl number of saturated liquid as function of the pressure					P =	1	bar
Function PrL_P(p)					'7.12.- Prandtl number of saturated liquid as function of the pressure
					Function PrL_P(p)
PrL_P = Pr_pT(p, (Tsat_p(p) - 0.1))
					PrL_P = Pr_pT(p, (Tsat_p(p) - 0.1))
End Function					PrL_P(p)	PrL_P(p)
					PrL_P(p)	1,76	-		End Function

'7.13.- Prandtl number of saturated liquid as function of the temperature					T =	99,61	ºC
					'7.13.- Prandtl number of saturated liquid as function of the temperature
Function PrL_t(t)
					Function PrL_t(t)
PrL_t = Pr_pT((psat_T(t) + 0.1), t)
					PrL_t = Pr_pT((psat_T(t) + 0.1), t)
End Function					PrL_t(t)	PrL_t(t)
					PrL_t(t)	1,76	-		End Function

'7.14.- Prandtl number of saturated vapor as function of the pressure
					P =	1	bar		'7.14.- Prandtl number of saturated vapor as function of the pressure
Function PrV_P(p)
					Function PrV_P(p)
PrV_P = Pr_pT(p, (Tsat_p(p) + 0.1))
					PrV_P = Pr_pT(p, (Tsat_p(p) + 0.1))
End Function					PrV_P(p)	PrV_P(p)
					PrV_P(p)	1,03	-		End Function

'7.15.- Prandtl number of saturated vapor as function of the temperature					T =	99,61	ºC
					'7.15.- Prandtl number of saturated vapor as function of the temperature
Function PrV_t(t)
					Function PrV_t(t)
PrV_t = Pr_pT((psat_T(t) - 0.1), t)
					PrV_t = Pr_pT((psat_T(t) - 0.1), t)
End Function					PrV_t(t)	PrV_t(t)
					PrV_t(t)	1,02			End Function

'7.16.- Specific volume in the humid region as function of pressure and dryness					P =	10	bar
					X =	0,8	-		'7.16.- Specific volume in the humid region as function of pressure and dryness
Function v_px(p, X)
					Function v_px(p, X)
v_px = vL_p(p) + X * (vV_p(p) - vL_p(p))
					v_px = vL_p(p) + X * (vV_p(p) - vL_p(p))
End Function					v_px(p, X)	v_px(p, X)
					v_px(p, X)	0,16	m3/kg		End Function

'7.17.- Specific volume in the humid region as function of temperature and dryness					T =	179,89	ºC
					X =	0,8	-		'7.17.- Specific volume in the humid region as function of temperature and dryness
Function v_tx(t, X)
					Function v_tx(t, X)
v_tx = vL_T(t) + X * (vV_T(t) - vL_T(t))
					v_tx = vL_T(t) + X * (vV_T(t) - vL_T(t))
End Function					v_tx(t, X)	v_tx(t, X)
					v_tx(t, X)	0,16			End Function

'7.18.- Vapourisation Heat as a function of the pressure					P =	10	bar
					'7.18.- Vapourisation Heat as a function of the pressure
Function hfg_p(p)
					Function hfg_p(p)
hfg_p = hV_p(p) - hL_p(p)
					hfg_p = hV_p(p) - hL_p(p)
End Function					hfg_p(p)	hfg_p(p)
					hfg_p(p)	2014,44	kJ/kg		End Function

'7.19.- Vapourisation Heat as a function of the temperature

Function hfg_t(t)					T =	179,89	ºC
					'7.19.- Vapourisation Heat as a function of the temperature
hfg_t = hV_T(t) - hL_T(t)
					Function hfg_t(t)
End Function
					hfg_t = hV_T(t) - hL_T(t)
					hfg_t(t)	hfg_t(t)
					hfg_t(t)	2014,42			End Function

'7.20.- Dryness in the humid region as function of temperature and entropy					P =	10	bar
					X =	0,8	-		'7.20.- Dryness in the humid region as function of temperature and entropy
Function x_ts(t, s)					Tsat_p =	179,89	ºC
					h_px =	2374,2	kJ/kg		Function x_ts(t, s)
x_ts = (s - sL_T(t)) / (sV_T(t) - sL_T(t))					s_pH =	5,7	kJ/(kg K)
					x_ts = (s - sL_T(t)) / (sV_T(t) - sL_T(t))
End Function					x_ts(t, s)	x_ts(t, s)
					x_ts(t, s)	0,8			End Function

'========================================================

## Turbine stage
				Rev. cjc. 06.04.2017

Application to a turbine stage

Turbine stage
Input data is in yelow cells, calculated values in green cells
Steam properties [1]
Input data:
Steam pressure before stage	p1 =	61	kPa
Steam temperature before stage	t1 =	450	°C
Pressure after stage	p2 =	4,3	kPa
Stage isentropic efficiency	hs =	0,87	-

Calculated values:
Inlet enthalpy	h1 =	h_PT =	3301,3	kJ/kg
Inlet entropy	s1 =	s_PT =	6,71	kJ/kg.K
Outlet isentropic entropy	s2s =	s1	6,71	kJ/kg.K
Outlet isentropic enthalpy	h2s =	h_Ps =	2674,8	kJ/kg
Isentropic power generation	Dhs =	h1 - h2s	626,5	kJ/kg
Real power generation	Dh =	Dhs * hs	545,1	kJ/kg
Specific energy (Ditto)	Espec =	Dh [kJ/kg) * 1000 [kg/h] /3600	151,4	kWh/ton
Outlet steam enthalpy	h2 =	h1 - Dh	2756,2	kJ/kg
Outlet steam temperature	t2 =	t_Ph =	152,6	°C
Outlet saturation temperature	t2sat =	tSat_P =	146,2	°C
Outlet steam superheating	Dtout,superheat =	t2 - t2sat =	6,4	°C
Outlet steam entropy	s2 =	s_PT =	6,91	kJ/kg.K

## Pressure Reducing Valve
Application to desuperheating

Calculation of a pressure reducing valve, PRV, with desuperheating
Input data is in yellow cells.
Water and steam properties calculated with [1]
Input data:
Steam pressure before PRV	p1 =	62	bar
Steam temperature before PRV	t1 =	450	°C
Steam pressure after PRV	p2 =	4,3	bar
Steam temperature after PRV and desuperheating (2)	t2 =	165	-
Desuperheater water pressure	p4 =	30	bar
Desuperheater water temperature, in feed tank	t3 =	130	°C
Desuperheater water pump efficiency	hp =	0,74	-
Pump motor efficiency	hm =	0,94	-
High pressure steam flow	ms =	75,0	ton/h

Note 2. Cooled, but still a superheated steam

Calculated data:

Steam properties
Inlet steam entalpy	h1 =	h_pt =	3.300	kJ/kg
Outlet steam enthalpy	h2 =	h_pt =	2.784	kJ/kg
Entropy at steam inlet conditions (p1, t1)	s1 =	s_pt =	6,70	kJ/(kg*K)
Entropy at steam outlet conditions (p2, t2)	s2 =	s_pt =	6,97	kJ/(kg*K)
Entropy at pressure "p1", in saturated condition	s1,sat =	sV_P =	5,87	kJ/(kg*K)
Temperature at pressure "p1", in saturated condition	t1,sat =	tSat_P =	278	ºC
Saturated steam entropy at "p2"	s2,sat =	sV_P =	6,87	kJ/(kg*K)
Saturated steam temperature at "p2"	t2,sat =	tSat_P =	146	ºC
Temperature after isentalpic expansion (h1) to "p2"	t1a =	t_Ph =	503	ºC

Feed water tank with saturated water at t3
Desuperheater water enthalpy (in feed water tank)	h3 =	hL_T =	546	kJ/kg
Pressure in feed water tank	p3 =	pSat_T =	2,7	bar
Water entropy in feed water tank	s3 =	sL_T =	1,6	kJ/(kg*K)

Feed water pump					Pump shaft power
Water entropy after pump, isentropic process	s4o =	s3	1,6	kJ/(kg*K)			(The pump is calculated in the same way as a compressor would have been)
Isentropic outlet entalpy	h4o =	h_ps	549	kJ/kg					Pshaft =	mw*Dh
Isentropic pump power demand:	Dhs =	h4o - h3	2,9	kJ/kg			Feed water flow rate				mw =	4,8	kg/s
Real pump specific power demand					Specific power demand for the water compresion				Dh =	4,0	kJ/kg
Water pump efficiency	hp =	Dh / Dhs	0,74	-			Pump shaft power				Pshaft =	mw*Dh
Specific power demand for the water compresion	Dh =	Dhs / hp	4,0	kJ/kg					Pshaft =	19,1	kW

Properties of desuperheating water, at PRV inlet (state "4")					Electrical pump power				PElec =	Pshaft / hm
Water outlet enthalpy	h4 =	h3 + Dh					Pump shaft power				Pshaft =	19,1	kW
	h3 =		546	kJ/kg			Motor efficiency				hm =	0,94	-
	Dh =		4,0	kJ/kg			Electrical pump power				PElec =	Pshaft /hm
	h4 =	h3 + Dh	550	kJ/kg					PElec =	20,3	kW
Water temperature at PRV inlet	t4 =	T_Ph	130,5	ºC

					Pump power can also be calculated as: (the normal way)
Energy balance		Ein =	Eout				Water specific volume at inlet				v =	SaturWater_SpecVolume_t(t3)
		ms * h1 + mw * h4 =	ms *h2 + mw * h2					v =	0	m3/kg
		ms * (h1 - h2) =	mw * (h2 - h4)				Water density				rw =	1 / v
		mw =	ms * (h1 - h2) / (h2 - h4)					rw =	934,6	kg/m3
					Water mass flow rate				mw =	ms * (h1 - h2) / (h2 - h4)
	Let	rh=	(h1 - h2) / (h2 - h4)					mw =	4,8	kg/s
		h1 =	3.300	kJ/kg			Water volume flow rate				Qw =	mw / rw
		h2 =	2.784	kJ/kg					Qw =	0,0051	m3 /s
		h4 =	550	kJ/kg			Pump pressure increase				Dp =	p4 - p3
		rh=	0,231	-					Dp =	27,30	bar
	thus					Desuperheater water pump efficiency				hp =	0,74	-
		mw =	ms * rh				Pump shaft power				Pshaft =	Qw*Dp/hp
					Pshaft =	19,0	kW
					Motor efficiency				hm =	0,94	-
Required water per 1 kg of HP steam	mw,1 =	ms1 * rh					Electrical pump power				PElec =	Pshaft / hm
	ms1 =	1	kg s					PElec =	20,2	kW
	rh=	0,231	-
	mw,1 =	0,231	kg w / kg s

Water mass flow rate	mw =	ms * (h1 - h2) / (h2 - h4)
	mw =	ms * rh
	ms =	75,0	ton h
	ms =	20,83	kg/s
	rh=	0,231	-
	mw =	ms * rh
	mw =	17,3	ton/h
	mw =	4,8	kg/s

Low pressure steam flow rate	ms_LP =	ms + mw
	ms =	20,8	kg/s
	mw =	4,8	kg/s
	ms_LP =	25,6	kg/s
	ms_LP =	92,3	ton/h

## Enthalpy change
Enthalpy and temperature change in a compression process for a given pressure increment

	For a compression			Thus			Units
	Pshaft =	mw*Dh		mw*Dh =	Qw*Dp/hs		Dh =	Dp/rw	[Pa * m3/kg ]		The actual change of enthalpy [J / kg] in a
	Pshaft =	Qw*Dp/hs		Qw*rw*Dh =	Qw*Dp/hs				[N/m2 * m3/kg ]		compression process is equivalent to the
				rw*Dh =	Dp/hs				[N * m/kg ]		pressure increment [Pa] divided by the
				Dh =	(Dp/rw)/hs				[J/kg ]		density [kg / m3] and the efficiency.

	Application				Pressure increment
	Fluid:	Water			DP =	267	ft wc	Real enthalpy change				Power loss to the fluid
	Pressure				DP =	81	mwc	Dh =	(Dp/rw)/hs			DhLoss =	Dhs * (1-hs)/hs
	DP =	267	ft wc		DP =	797.085	Pa	DP =	797.085	Pa		Dhs =	0,799	kJ/kg
	Water density				DP =	8,0	bar	rw =	998	kg/m³		hs =	0,6
	rw =	998	kg/m³					hs =	0,6			DhLoss =	0,532	kJ/kg
	Pump isentropic efficiency				Ideal enthalpy change			Dh =	1.331	J/kg
	hs =	0,6	-		Dhs =	(Dp/rw)		Dh =	1,331	kJ/kg		Fluid temperature increment
	Water specific heat				DP =	797.085	Pa					DhLoss =	cp * Dt
	cp =	4,182	kJ/(kg * K)		rw =	998	kg/m³	Dhloss=	Dh - Dhs	kJ/kg		Dt =	DhLoss / cp
					Dhs =	798,7	J/kg	Dh =	1,331	kJ/kg		DhLoss =	0,532	kJ/kg
					Dhs =	0,799	J/kg	Dhs =	0,799	kJ/kg		cp =	4,182	kJ/(kg * K)
	g =	9,81	m/s²					DhLoss =	0,532	kJ/kg		Dt =	0,13	K

	Example using the functions
					Isentropic compression				Real enthalpy change
	P1 =	1,01	bar		s2 =	s1			Dh =	Dhs / h		Outlet temperature
	t1 =	22	ºC		s2 =	0,325	kJ/(kg*K)		Dhs =	0,805		P2 =	9,01	bar
					h =	0,6	-	h2 =	93,72	kJ/kg
	P2 =	P1 + DP			Inlet enthalpy				Dh =	1,341	kJ/kg	t2 =	22,16	kJ/kg
	P1 =	1,01	bar		h1 =	h_PT
	DP =	8	bar		h1 =	92,38	kJ/kg		Outlet enthalpy			Temperature increment during
	P2 =	9,01	bar					h2 =	h1 + Dh		the compresion of the liquid
					Isentropic outlet enthalpy				h1 =	92,38	kJ/kg	Dt =	t2 -t1
	h =	0,6	-		h2,0 =	93,19	kJ/kg		Dh =	1,341	kJ/kg	t2 =	22,16	ºC
					h2 =	93,72	kJ/kg	t1 =	22	ºC
	s1 =	s_PT			Isentropic enthalpy change					Dt =	0,16	ºC
	s1 =	0,325	kJ/(kg*K)		Dhs =	h2,0 -h1			Dhloss=	Dh - Dhs	kJ/kg
					h2,0 =	93,19	kJ/kg		Dh =	1,341	kJ/kg
					h1 =	92,38	kJ/kg		Dhs =	0,805	kJ/kg
					Dhs =	0,805	kJ/kg		DhLoss =	0,536	kJ/kg

	rw			Cp
	P1 =	1,01	bar	P1 =	1,01	bar					g =	9,81	m/s²
	t1 =	22	ºC	t1 =	22	ºC
	r1 =	997,8	kg/m³	Cp1 =	4,1835	kJ/(kg*K)

	P2 =	9,01	bar	P2 =	9,01	bar
	t2 =	22,16	ºC	t2 =	22,16	ºC
	r2 =	998,1	kg/m³	Cp2 =	4,1810	kJ/(kg*K)

	r =	997,9	kg/m³	Cp =	4,182	kJ/(kg*K)

## Pipe friction
Pressure loss in a steam pipe				Inside pipe diameter				Kinematic viscosity of saturated steam				Friction factor
				di =	Pipe_Imp_CS_Dint_dn_sch			n =	nyV_P			f =
Saturated steam at pressure "Pg", in a				dn =	10	in		n =	3,3E-06	m²/s		Rrel =	0,00004	-
locality with a height above sea level "H".				sch =	STD							Re =	2,70E+06	-
Carbon steel pipe with nominal diameter				di =	254,5	mm		Volumetric flow rate				f =	0,011	-
"dn", schedule "sch" and absolute				di =	0,254	m		V =	m / r
rugosity "Rabs".								m =	8	kg/s		Unit pressure loss
Steam mass flow rate "m".				Pipe section area				r =	4,54	kg/m³		J =	f * (1 / di) * hv
Pipe equivalent length "Leq".				A =	(p/4)*di^2			V =	1,76	m³/s		f =	0,011	-
				di =	0,25	m						di =	0,25	m
Pg =	8	bar(g)		A =	0,0509	m²		Flow velocity (Note 1)				hv =	2726,3	Pa
H =	2300	m.s.n.m.						v =	V / A			J =	120,5	Pa/m
dn =	10	in		Relative rugosit				V =	1,76	m³/s
sch =	STD	-		Rrel =	Rabs / di			A =	0,05085	m²		Pressure loss
Rabs =	0,01	mm		Rabs =	0,01	mm		v =	34,7	m/s		DP =	J * Leq
m =	8	kg/s		di =	254,46	mm		OK. Velocity within range				J =	120,5	Pa/m
Leq =	500	m		Rrel =	0,00004	-						Leq =	500	m
								Kinematic pressure				DP =	60.234	Pa
				Steam properties				hv =	(r/2) * v²			DP =	60,2	kPa
Local atmospheric pressure				Entropy				r =	4,5	kg/m³
Patm = 101,325* (1 -2,25577E-5 * H)^5,25588				s =	sV_P			v =	34,7	m/s		Pressure loss in 100 m
H =	2300	m.a.s.l.		P =	8,77	bar		hv =	2726	Pa		DP100 m =	J * 100
patm =	0,77	bar		s =	6,63	kJ/(kg*K)						J =	120,5	Pa/m
								Reynolds number				L =	100	m
				Temperature				Re =	v * d / n			DP100 m =	12.047	Pa/(100 m)
Absolute pressure				t =	tSat_P			v =	34,7	m/s		DP100 m =	12,0	kPa/(100 m)
P =	patm + Pg			p =	8,77	bar		di =	0,25	m
patm =	0,77	bar		t =	174,2	ºC		n =	3,3E-06	m²/s		Saturated steam recommended
Pg =	8	bar(g)						Re =	2,7E+06	-		acceptable pressure drop [2]
P =	8,77	bar		Density								103 kPa < P < 700 kPa
				r =	rhoV_P							kPa / 100 m
Note: Properties [3]				r =	4,5	kg/m³						11,31	45,24

												Pressure loss per 100 m
Note (1)	According [2], for saturated steam with pressure in the range 1 to 7 bar (g),											DP100m =	12,05	kPa / 100 m
	the recommended velocity is in the range 10 to 38 m/s.											OK.Pressure loss within range
	and the pressure drop in the range 0.11 to 0.34 bar / 100m

## Recommende v and dP
				Saturated steam
http://www.watsonmcdaniel.com/2011Catalog/EngineeringData.pdf					103 kPa(g) < P < 700 kPa(g)
				kPa / 100 m
Recommended velocities and pressure drops for					11,31	45,24		Recommended velocities and pressure drops for
various services [2]					various services [2]
Service			Velocity		Pressure drops					Service			Velocity		Pressure drops
			m/s		bar/100 m		kPa / 100 m					ft/min		psi/100 ft
Saturated steam					Saturated steam
Vacuum			10	20	0,0566	0,1131	5,66	11,31			Vacuum			2.000	4.000	0,25	0,5
0 - 1.03 bar (g)			10	25	0,0566	0,1131	5,66	11,31			0 - 15 psig			2.000	5.000	0,25	0,5
1.03 - 7 bar (g)			10	38	0,1131	0,3393	11,31	33,93			15 - 100 psig			2.000	7.500	0,5	1,5
Over 7 bar (g)			10	46	0,1131	0,4524	11,31	45,24			Over 100 psig			2.000	9.000	0,5	2
Steam Main, Low noise			20	30					Steam Main, Low noise			4.000	6.000
Steam Main, Industrial Plant			41	61					Steam Main, Industrial Plant			8.000	12.000
Superheated Steam					Superheated Steam
0 - 7 bar (g)			13	51	0,11	0,34					0- 100 psig			2.500	10.000	0,5	1,5
7 - 35 bar (g)			13	61	0,23	0,45					100 - 500 psig			2.500	12.000	1	2
Condensate					Condensate			ft/sec
Boiler feed pump suction			0,46	0,76					Boiler feed pump suction			1,5	2,5
Condensate pump suction			0,46	0,91					Condensate pump suction			1,5	3
Condensate pump discharge			0,91	2,29					Condensate pump discharge			3	7,5
Boiler feed pump discharge			1,22	3,05					Boiler feed pump discharge			4	10
Hot water (quiet flow)					Hot water (quiet flow)			ft/sec
Heating systems			1,22					Heating systems			4
Pump suction lines			0,30	2,44					Pump suction lines			1	8
Pump discharge lines			1,52	4,57					Pump discharge lines			5	15
Cooling water systems			1,52	4,57					Cooling water systems			5	15

According [2], for saturated steam with pressure in the range 1 to 7 bar (g),					1 ft/min =	0,01	m/s	1 psi /100 ft =	0,07	bar/100 ft
the recommended velocity is in the range 10 to 38 m/s.					FtMin =	0,01		1 psi /100 ft =	0,07	bar/30.48 m
and the pressure drop in the range 0.11 to 0.34 bar / 100m					1 ft/sec =	0,3		1psi /100 ft =	0	bar/m
				FtSec =	0,3		1 psi /100 ft =	0,23	bar/100 m
				PsiBar =	0,23

## Ref1
[1]	Water and steam properties according to IAPWS IF-97
	By Magnus Holmgren
	www.x-eng.com

	Thermodynamic properties
	Thermodynamic properties (according to IAPWS IF-97 )
	Release on the IAPWS Industrial Formulation 1997 for the
	Thermodynamic Properties of Water and Steam 1997

	Transport properties
	Viscosity (IAPWS formulation 1985)
	Thermal Conductivity (IAPWS formulation 1985)
	Revised release on the IAPS Formulation 1985 for the
	Thermal Conductivity of ordinary water IAPWS
	September 1998 Page 8
	Surface Tension ('IAPWS Release on Surface Tension
	of Ordinary Water Substance September 1994)					https://www.mathworks.com/matlabcentral/fileexchange/9817-x-steam--thermodynamic-properties-of-water-and-steam

[2]	Engineering Data
	Watson McDaniel
	http://www.watsonmcdaniel.com/2011Catalog/EngineeringData.pdf